## Configurations
#Name CCU2 (Database) | Art der Aenderung | #description | unit, dataType, boundaries, default |  |  |  |  | Page on HMI ( " ." means subpage ) | Send to R5
Layer | [9 empty] | Layer: | A53::DataLayer | A53::PresentationLayer |  | A53::BusinessLayer |  |  |  | A53::middlewarelayer (name not decided yet) | R5::ConfigurationLayer | R5::BusinessLayer | R5::HW-MiddlewareLayer
row eingefügt
modules/ value-boundaries |  |  | #unit | #datatype | #min | #max | #default |  |  | Module: | §DataBaseModule | §GridConBackendModule | §ModbusModule | §CommunicationHandlerModule | §ErrorHandlerModule | §MeasurementsA53Module | §StatemachineModule | §DSCLibA53Module | module is not planned yet | §ControlModule | §ActorModule | §MioModule | §DSCLibR5Module
#ConfigSystem
acdcActorNumber |  | number of connected acdc-dsc-clients |  | int | 0 | 12 | 1 | System.DSC.Number of IPU |  |  | s | r | r |  | r | r | r | r |  | r | r |  | r
mioNumber |  | number of connected mio-dsc-clients |  | int | 0 | 6 | 1 | System.DSC.Number of MIO |  |  | s | r | r |  | r | r |  | r |  |  |  |  | r
#ConfigGrid
nominalFrequency |  | of the connected grid (gridMeasurementPoint 1 and 2) | Hz | float | 45.0f | 65.0f | 50.0f | System.grid.nominal frequency | yes |  | s | r | r |  | r | r |  |  |  | r
voltageMeasurement2Enabled |  | 2 means gridMeasurementPoint 2 |  | int | 0 | 1 | 0 | n.a. |  |  | s | r |  |  |  | r |  |  |  | r |  | r (inspector)
nominalVoltage1 |  | of the connected grid (measurementPoint 1 ) | V | float | 20.0f | 100000.0f | 400.0f | System.grid.Nominal voltage |  |  | s | r | r |  | r | r | r |  |  | r
nominalVoltage2 |  | of the connected grid (measurementPoint 2 ) | V | float | 200.0f | 1000000.0f | 400.0f | n.a. |  |  | s | r | r | [6 empty] | r
starOrDeltaMeasurement1 |  | TN, IT |  | int | 0 | 1 | 0 | System.grid.grid configuration |  |  | s | r | s/r (optional) |  |  | r | [5 empty] | r(inspector)
openOrClosedLoop |  | openLoop closedLoop |  | int | 0 | 1 | 0 | System.grid.Control topology |  |  | s | r | s/r (optional) | [6 empty] | r
#ConfigErrorHandler
dcVoltageSumMax |  | max. of dcLink (boundary for inspector) not in use | V | float | 0.0f | 100000.0f | 0.0f | n.a. | no |  | s | r |  |  | r
dcVoltageSumMin |  | min. of dcLink (boundary for inspector) not in use | V | float | 0.0f | 100000.0f | 0.0f | n.a. |  |  | s | r |  |  | r
thduLimit |  | max. of voltage total harmonic distortion (boundary for inspector) | % | int | 0 | 100 | 20 | system.grid.level thdv for shutdown |  |  | s | r |  |  | r | r
ipuRedundancy |  | the errorhandler needing this info if he has to switch down system in case of actor error |  | int | 0 | 1 | 0 | n.a. |  |  | s | r |  |  | r
#ConfigDatabase
activeParametersetAfterBooting |  | a) could not be placed in the params cause it is needed after booting which paramset has to be initialized b) able to switch between whole parameterSets (goal: not every param hast to be changed one by one) c) checkout polarion: Project Änderungsdienst ACF : PQAA-1456 HMI Kopfzeile Statusanzeige und Parametersatzumschaltung |  | int | 1 | 8 | 1 | n.a. | no |  | r | r
#ConfigEventRecorder
enabled |  | 0: disabled 1: enabled: logger writes values to persistent memory if triggered |  | int | 1 | 0 | 1 | n.a. | no |  | s (r: not decided yet where the module will be placed) | r
afterTrigger |  | How many values (in percent) have to be stored after the trigger event |  | float | 0.0f | 1.0f | 0.2f | n.a. |  |  | s (r: not decided yet where the module will be placed) | r
prescaler |  | Scales length of errorbin-file Prescaler Memory lengthOfErrorBin 1 892 kB 200 ms 2 1780 kB 400ms . . . 5 4444 kB 1 s |  | int | 1 | 5 | 1 | n.a. |  |  | s (r: not decided yet where the module will be placed) | r
#ConfigStatemachine
autostart_enabled |  | 0: disabled 1: enabled |  | int | 0 | 1 | 0 | control.Basic Setting.Auto Features.Automatic Start.value | no |  | s | r |  |  |  |  | r
autostart_timeout |  | checkout Polarion: Projekt: Änderungsdienst ACF Ticket: PQAA-3134 Autofunktionen ACF | s | int | 0 | 600 | 60 | control.Basic Setting.Auto Features.Automatic Start.time |  |  | s | r |  |  |  |  | r
powersave_mode |  | checkout Polarion: Projekt: Änderungsdienst ACF Ticket: PQAA-1564 Powersaving not in use |  | int | 0 | 3 | 0 | n.a. |  |  | s | r |  |  |  |  | r
powersave_delayIdleEntry |  |  |  | float | 60.0f | 86400.0f | 300.0f | n.a. |  |  | s | r |  |  |  |  | r
powersave_delayIdleLeave |  |  |  | float | 1.0f | 86400.0f | 1.0f | n.a. |  |  | s | r |  |  |  |  | r
powersave_delayEcoEntry |  |  |  | float | 30.0f | 3600.0f | 60.0f | n.a. |  |  | s | r |  |  |  |  | r
powersave_delayEcoLeave |  |  |  | float | 1.0f | 3600.0f | 1.0f | n.a. |  |  | s | r |  |  |  |  | r
powersave_thresholdCurrentEntry |  |  |  | float | 3.0f | 100.0f | 5.0f | n.a. |  |  | s | r |  |  |  |  | r
powersave_thresholdCurrentLeave |  |  |  | float | 4.0f | 10.0f | 10.0f | n.a. |  |  | s | r |  |  |  |  | r
sia_triggerAfterBootEnabled |  | 0: disabled 1: trigger Sia automatically after first entry in Run or Pause after Booting |  | int | 0 | 1 | 0 | n.a. |  |  | s | r |  |  |  |  | r
autoRestart_maxCount |  | maximum restarts attempts after error checkout Polarion: Project: Änderungsdienst ACF: PQAA-1604 Schutz - Auto Restart nach Fehler |  | int | 0 | 7 | 0 | n.a. |  |  | s | r |  |  |  |  | r
#ConfigMio
_1_measurement_ct1_primary |  |  | A | float | -100000000 | 100000.f | 1.f | system.schnittstellen.digital E/A DSC Port 0.ctC.primary |  |  | s | r | [9 empty] | r
_1_measurement_ct1_1Aor5ARange |  | 0: 1A range 1: 5A range | A | int | 0 | 1 | 0 | system.schnittstellen.digital E/A DSC Port 0.ctC.secondary |  |  | s | r | [9 empty] | r
_1_measurement_ct2_primary |  |  | A | float | -100000000 | 100000.f | 1.f | system.schnittstellen.digital E/A DSC Port 0.ctC.primary |  |  | s | r | [9 empty] | r
_1_measurement_ct2_1Aor5ARange |  | 0: 1A range 1: 5A range | A | int | 0 | 1 | 0 | system.schnittstellen.digital E/A DSC Port 0.ctC.secondary |  |  | s | r | [9 empty] | r
_1_measurement_ct3_primary |  |  | A | float | -100000000 | 100000.f | 1.f | system.schnittstellen.digital E/A DSC Port 0.ctC.primary |  |  | s | r | [9 empty] | r
_1_measurement_ct3_1Aor5ARange |  | 0: 1A range 1: 5A range | A | int | 0 | 1 | 0 | system.schnittstellen.digital E/A DSC Port 0.ctC.secondary |  |  | s | r | [9 empty] | r
_1_measurement_ct4_primary |  |  | A | float | -100000000 | 100000.f | 1.f | system.schnittstellen.digital E/A DSC Port 0.ctC.primary |  |  | s | r | [9 empty] | r
_1_measurement_ct4_1Aor5ARange |  | 0: 1A range 1: 5A range | A | int | 0 | 1 | 0 | system.schnittstellen.digital E/A DSC Port 0.ctC.secondary |  |  | s | r | [9 empty] | r
_1_measurement_ct1_current_Input |  | 0: OFF 1: IL1_1 2: IL2_1 3: IL3_1 |  | int | 0 | 3 | 1 | eingang.x6.1 |  |  | s | r | [9 empty] | r
_1_measurement_ct2_current_Input |  | 0: OFF 1: IL1_1 2: IL2_1 3: IL3_1 |  | int | 0 | 3 | 2 | eingang.x6.2 |  |  | s | r | [9 empty] | r
_1_measurement_ct3_current_Input |  | 0: OFF 1: IL1_1 2: IL2_1 3: IL3_1 |  | int | 0 | 3 | 3 | eingang.x6.3 |  |  | s | r | [9 empty] | r
_1_measurement_ct4_current_Input |  | 0: OFF 1: IL1_1 2: IL2_1 3: IL3_1 |  | int | 0 | 3 | 0 | eingang.x6.4 |  |  | s | r | [9 empty] | r
_1_io0_measurement_vtCircuit |  | 0 -> only measuring 1 -> U23 will be calculated 2 -> U31 will be calculated 3 -> U12 will be calculated | A | int | 0 | 3 | 0 | n.a. |  |  | s | r | [9 empty] | r
_1_measurement_vt1_primary |  |  | V | float | -100000000 | 100000000.f | 1000.f | system.schnittstellen.digital E/A DSC Port 0.vtV.primary |  |  | s | r | [9 empty] | r
_1_measurement_vt1_100Vor1000VRange |  | 0: 100V range 1: 1000V range | V | int | 0 | 1 | 1 | system.schnittstellen.digital E/A DSC Port 0.vtV.secondary |  |  | s | r | [9 empty] | r
_1_measurement_vt2_primary |  |  | V | float | -100000000 | 100000000 | 1000.f | system.schnittstellen.digital E/A DSC Port 0.vtV.primary |  |  | s | r | [9 empty] | r
_1_measurement_vt2_100Vor1000VRange |  | 0: 100V range 1: 1000V range | V | int | 0 | 1 | 1 | system.schnittstellen.digital E/A DSC Port 0.vtV.secondary |  |  | s | r | [9 empty] | r
_1_measurement_vt3_primary |  |  | V | float | -100000000 | 100000000.f | 1000.f | system.schnittstellen.digital E/A DSC Port 0.vtV.primary |  |  | s | r | [9 empty] | r
_1_measurement_vt3_100Vor1000VRange |  | 0: 100V range 1: 1000V range | V | int | 0 | 1 | 1 | system.schnittstellen.digital E/A DSC Port 0.vtV.secondary |  |  | s | r | [9 empty] | r
_1_measurement_temperatureSensortype |  | TEMPSENSOR_NOT_USED = 0, TEMPSENSOR_MIO_KTY81 = 1, // MIO Ext. Temp KTY81-110 or -120 TEMPSENSOR_MIO_KTY84 = 2, // MIO Ext. Temp KTY84-130 TEMPSENSOR_MIO_PT1000 = 4, // MIO Ext. Temp PT1000 not in use |  | int | 0 | 3 | 0 | system.schnittstellen.digital E/A DSC Port 0.temperatur measurement (ext.) |  |  | s | r | [9 empty] | r
_1_inspector_extTempMin |  | lower boundary of the temperature measurement in the mio checkout Polarion: Project: Änderungsdienst ACF: PQAA-1598 Schutz - Externe Überwachung not in use | °C | float | -100 | 250.f | 250.f | n.a. |  |  | s | r | [9 empty] | r
_1_inspector_extTempMax |  | upper boundary of the temperature measurement in the mio checkout Polarion: Project: Änderungsdienst ACF: PQAA-1598 Schutz - Externe Überwachung not in use | °C | float | -100 | 250.f | 250.f | n.a. |  |  | s | r | [9 empty] | r
_1_inspector_LCUTempMin |  | lower boundary of the liquid cooled temperature measurement checkout Polarion: Project: Änderungsdienst ACF: PQAA-1565 Wasserkühlung not in use | °C | float | 100.f | 30.f | -20 | n.a. |  |  | s | r | [9 empty] | r
_1_inspector_LCUTempMax |  | upper boundary of the liquid cooled temperature measurement checkout Polarion: Project: Änderungsdienst ACF: PQAA-1565 Wasserkühlung not in use | °C | float | 0 | 90.f | 30.f | n.a. |  |  | s | r | [9 empty] | r
_2_measurement_ct1_primary |  |  | A | float | -100000 | 100000.f | 1.f | system.schnittstellen.digital E/A DSC Port 0.ctC.primary |  |  | s | r | [9 empty] | r
_2_measurement_ct1_1Aor5ARange |  | 0: 1A range 1: 5A range | A | int | 0 | 1 | 0 | system.schnittstellen.digital E/A DSC Port 0.ctC.secondary |  |  | s | r | [9 empty] | r
_2_measurement_ct2_primary |  |  | A | float | -100000 | 100000.f | 1.f | system.schnittstellen.digital E/A DSC Port 0.ctC.primary |  |  | s | r | [9 empty] | r
_2_measurement_ct2_1Aor5ARange |  | 0: 1A range 1: 5A range | A | int | 0 | 1 | 0 | system.schnittstellen.digital E/A DSC Port 0.ctC.secondary |  |  | s | r | [9 empty] | r
_2_measurement_ct3_primary |  |  | A | float | -100000 | 100000.f | 1.f | system.schnittstellen.digital E/A DSC Port 0.ctC.primary |  |  | s | r | [9 empty] | r
_2_measurement_ct3_1Aor5ARange |  | 0: 1A range 1: 5A range | A | int | 0 | 1 | 0 | system.schnittstellen.digital E/A DSC Port 0.ctC.secondary |  |  | s | r | [9 empty] | r
_2_measurement_ct4_primary |  |  | A | float | -100000 | 100000.f | 1.f | system.schnittstellen.digital E/A DSC Port 0.ctC.primary |  |  | s | r | [9 empty] | r
_2_measurement_ct4_1Aor5ARange |  | 0: 1A range 1: 5A range | A | int | 0 | 1 | 0 | system.schnittstellen.digital E/A DSC Port 0.ctC.secondary |  |  | s | r | [9 empty] | r
_2_measurement_ct1_current_Input |  | 0: OFF 1: IL1_1 2: IL2_1 3: IL3_1 |  | int | 0 | 3 | 0 | eingang.x6.1 |  |  | s | r | [9 empty] | r
_2_measurement_ct2_current_Input |  | 0: OFF 1: IL1_1 2: IL2_1 3: IL3_1 |  | int | 0 | 3 | 0 | eingang.x6.2 |  |  | s | r | [9 empty] | r
_2_measurement_ct3_current_Input |  | 0: OFF 1: IL1_1 2: IL2_1 3: IL3_1 |  | int | 0 | 3 | 0 | eingang.x6.3 |  |  | s | r | [9 empty] | r
_2_measurement_ct4_current_Input |  | 0: OFF 1: IL1_1 2: IL2_1 3: IL3_1 |  | int | 0 | 3 | 0 | eingang.x6.4 |  |  | s | r | [9 empty] | r
_2_io0_measurement_vtCircuit |  | 0 -> only measuring 1 -> U23 will be calculated 2 -> U31 will be calculated 3 -> U12 will be calculated | A | int | 0 | 3 | 0 | n.a. |  |  | s | r | [9 empty] | r
_2_measurement_vt1_primary |  |  | V | float | -100000000 | 100000000.f | 1000.f | system.schnittstellen.digital E/A DSC Port 0.vtV.primary |  |  | s | r | [9 empty] | r
_2_measurement_vt1_100Vor1000VRange |  | 0: 100V range 1: 1000V range | V | int | 0 | 1 | 1 | system.schnittstellen.digital E/A DSC Port 0.vtV.secondary |  |  | s | r | [9 empty] | r
_2_measurement_vt2_primary |  |  | V | float | -100000000 | 100000000.f | 1000.f | system.schnittstellen.digital E/A DSC Port 0.vtV.primary |  |  | s | r | [9 empty] | r
_2_measurement_vt2_100Vor1000VRange |  | 0: 100V range 1: 1000V range | V | int | 0 | 1 | 1 | system.schnittstellen.digital E/A DSC Port 0.vtV.secondary |  |  | s | r | [9 empty] | r
_2_measurement_vt3_primary |  |  | V | float | -100000000 | 100000000.f | 1000.f | system.schnittstellen.digital E/A DSC Port 0.vtV.primary |  |  | s | r | [9 empty] | r
_2_measurement_vt3_100Vor1000VRange |  | 0: 100V range 1: 1000V range | V | int | 0 | 1 | 1 | system.schnittstellen.digital E/A DSC Port 0.vtV.secondary |  |  | s | r | [9 empty] | r
_2_measurement_temperatureSensortype |  | TEMPSENSOR_NOT_USED = 0, TEMPSENSOR_MIO_KTY81 = 1, // MIO Ext. Temp KTY81-110 or -120 TEMPSENSOR_MIO_KTY84 = 2, // MIO Ext. Temp KTY84-130 TEMPSENSOR_MIO_PT1000 = 4, // MIO Ext. Temp PT1000 not in use |  | int | 0 | 3 | 0 | system.schnittstellen.digital E/A DSC Port 0.temperatur measurement (ext.) |  |  | s | r | [9 empty] | r
_2_inspector_extTempMin |  | lower boundary of the temperature measurement in the mio checkout Polarion: Project: Änderungsdienst ACF: PQAA-1598 Schutz - Externe Überwachung not in use | °C | float | -100 | 250.f | 250.f | n.a. |  |  | s | r | [9 empty] | r
_2_inspector_extTempMax |  | upper boundary of the temperature measurement in the mio checkout Polarion: Project: Änderungsdienst ACF: PQAA-1598 Schutz - Externe Überwachung not in use | °C | float | -100 | 250.f | 250.f | n.a. |  |  | s | r | [9 empty] | r
_2_inspector_LCUTempMin |  | lower boundary of the liquid cooled temperature measurement checkout Polarion: Project: Änderungsdienst ACF: PQAA-1565 Wasserkühlung not in use | °C | float | 100 | 30.f | -20 | n.a. |  |  | s | r | [9 empty] | r
_2_inspector_LCUTempMax |  | upper boundary of the liquid cooled temperature measurement checkout Polarion: Project: Änderungsdienst ACF: PQAA-1565 Wasserkühlung not in use | °C | float | 0.f | 90.f | 30.f | n.a. |  |  | s | r | [9 empty] | r
_3_measurement_ct1_primary |  |  | A | float | -100000 | 100000.f | 1.f | system.schnittstellen.digital E/A DSC Port 0.ctC.primary |  |  | s | r | [9 empty] | r
_3_measurement_ct1_1Aor5ARange |  | 0: 1A range 1: 5A range | A | int | 0 | 1 | 0 | system.schnittstellen.digital E/A DSC Port 0.ctC.secondary |  |  | s | r | [9 empty] | r
_3_measurement_ct2_primary |  |  | A | float | -100000 | 100000.f | 1.f | system.schnittstellen.digital E/A DSC Port 0.ctC.primary |  |  | s | r | [9 empty] | r
_3_measurement_ct2_1Aor5ARange |  | 0: 1A range 1: 5A range | A | int | 0 | 1 | 0 | system.schnittstellen.digital E/A DSC Port 0.ctC.secondary |  |  | s | r | [9 empty] | r
_3_measurement_ct3_primary |  |  | A | float | -100000 | 100000.f | 1.f | system.schnittstellen.digital E/A DSC Port 0.ctC.primary |  |  | s | r | [9 empty] | r
_3_measurement_ct3_1Aor5ARange |  | 0: 1A range 1: 5A range | A | int | 0 | 1 | 0 | system.schnittstellen.digital E/A DSC Port 0.ctC.secondary |  |  | s | r | [9 empty] | r
_3_measurement_ct4_primary |  |  | A | float | -100000 | 100000.f | 1.f | system.schnittstellen.digital E/A DSC Port 0.ctC.primary |  |  | s | r | [9 empty] | r
_3_measurement_ct4_1Aor5ARange |  | 0: 1A range 1: 5A range | A | int | 0 | 1 | 0 | system.schnittstellen.digital E/A DSC Port 0.ctC.secondary |  |  | s | r | [9 empty] | r
_3_measurement_ct1_current_Input |  | 0: OFF 1: IL1_1 2: IL2_1 3: IL3_1 |  | int | 0 | 3 | 0 | eingang.x6.1 |  |  | s | r | [9 empty] | r
_3_measurement_ct2_current_Input |  | 0: OFF 1: IL1_1 2: IL2_1 3: IL3_1 |  | int | 0 | 3 | 0 | eingang.x6.2 |  |  | s | r | [9 empty] | r
_3_measurement_ct3_current_Input |  | 0: OFF 1: IL1_1 2: IL2_1 3: IL3_1 |  | int | 0 | 3 | 0 | eingang.x6.3 |  |  | s | r | [9 empty] | r
_3_measurement_ct4_current_Input |  | 0: OFF 1: IL1_1 2: IL2_1 3: IL3_1 |  | int | 0 | 3 | 0 | eingang.x6.4 |  |  | s | r | [9 empty] | r
_3_io0_measurement_vtCircuit |  | 0 -> only measuring 1 -> U23 will be calculated 2 -> U31 will be calculated 3 -> U12 will be calculated | A | int | 0 | 3 | 0 | n.a. |  |  | s | r | [9 empty] | r
_3_measurement_vt1_primary |  |  | V | float | -100000000 | 100000000.f | 1000.f | system.schnittstellen.digital E/A DSC Port 0.vtV.primary |  |  | s | r | [9 empty] | r
_3_measurement_vt1_100Vor1000VRange |  | 0: 100V range 1: 1000V range | V | int | 0 | 1 | 1 | system.schnittstellen.digital E/A DSC Port 0.vtV.secondary |  |  | s | r | [9 empty] | r
_3_measurement_vt2_primary |  |  | V | float | -100000000 | 100000000.f | 1000.f | system.schnittstellen.digital E/A DSC Port 0.vtV.primary |  |  | s | r | [9 empty] | r
_3_measurement_vt2_100Vor1000VRange |  | 0: 100V range 1: 1000V range | V | int | 0 | 1 | 1 | system.schnittstellen.digital E/A DSC Port 0.vtV.secondary |  |  | s | r | [9 empty] | r
_3_measurement_vt3_primary |  |  | V | float | -100000000 | 100000000 | 1000 | system.schnittstellen.digital E/A DSC Port 0.vtV.primary |  |  | s | r | [9 empty] | r
_3_measurement_vt3_100Vor1000VRange |  | 0: 100V range 1: 1000V range | V | int | 0 | 1 | 1 | system.schnittstellen.digital E/A DSC Port 0.vtV.secondary |  |  | s | r | [9 empty] | r
_3_measurement_temperatureSensortype |  | TEMPSENSOR_NOT_USED = 0, TEMPSENSOR_MIO_KTY81 = 1, // MIO Ext. Temp KTY81-110 or -120 TEMPSENSOR_MIO_KTY84 = 2, // MIO Ext. Temp KTY84-130 TEMPSENSOR_MIO_PT1000 = 4, // MIO Ext. Temp PT1000 not in use |  | int | 0 | 3 | 0 | system.schnittstellen.digital E/A DSC Port 0.temperatur measurement (ext.) |  |  | s | r | [9 empty] | r
_3_inspector_extTempMin |  | lower boundary of the temperature measurement in the mio checkout Polarion: Project: Änderungsdienst ACF: PQAA-1598 Schutz - Externe Überwachung not in use | °C | float | -100 | 250.f | 250.f | n.a. |  |  | s | r | [9 empty] | r
_3_inspector_extTempMax |  | upper boundary of the temperature measurement in the mio checkout Polarion: Project: Änderungsdienst ACF: PQAA-1598 Schutz - Externe Überwachung not in use | °C | float | -100 | 250.f | 250.f | n.a. |  |  | s | r | [9 empty] | r
_3_inspector_LCUTempMin |  | lower boundary of the liquid cooled temperature measurement checkout Polarion: Project: Änderungsdienst ACF: PQAA-1565 Wasserkühlung not in use | °C | float | 100.f | 30.f | -20 | n.a. |  |  | s | r | [9 empty] | r
_3_inspector_LCUTempMax |  | upper boundary of the liquid cooled temperature measurement checkout Polarion: Project: Änderungsdienst ACF: PQAA-1565 Wasserkühlung not in use | °C | float | 0.f | 90.f | 30.f | n.a. |  |  | s | r | [9 empty] | r
_4_measurement_ct1_primary |  |  | A | float | -100000000 | 100000000.f | 1 | system.schnittstellen.digital E/A DSC Port 0.ctC.primary |  |  | s | r | [9 empty] | r
_4_measurement_ct1_1Aor5ARange |  | 0: 1A range 1: 5A range | A | int | 0 | 1 | 0 | system.schnittstellen.digital E/A DSC Port 0.ctC.secondary |  |  | s | r | [9 empty] | r
_4_measurement_ct2_primary |  |  | A | float | -100000000 | 100000000.f | 1 | system.schnittstellen.digital E/A DSC Port 0.ctC.primary |  |  | s | r | [9 empty] | r
_4_measurement_ct2_1Aor5ARange |  | 0: 1A range 1: 5A range | A | int | 0 | 1 | 0 | system.schnittstellen.digital E/A DSC Port 0.ctC.secondary |  |  | s | r | [9 empty] | r
_4_measurement_ct3_primary |  |  | A | float | -100000000 | 100000000.f | 1 | system.schnittstellen.digital E/A DSC Port 0.ctC.primary |  |  | s | r | [9 empty] | r
_4_measurement_ct3_1Aor5ARange |  | 0: 1A range 1: 5A range | A | int | 0 | 1 | 0 | system.schnittstellen.digital E/A DSC Port 0.ctC.secondary |  |  | s | r | [9 empty] | r
_4_measurement_ct4_primary |  |  | A | float | -100000000 | 100000000.f | 1 | system.schnittstellen.digital E/A DSC Port 0.ctC.primary |  |  | s | r | [9 empty] | r
_4_measurement_ct4_1Aor5ARange |  | 0: 1A range 1: 5A range | A | int | 0 | 1 | 0 | system.schnittstellen.digital E/A DSC Port 0.ctC.secondary |  |  | s | r | [9 empty] | r
_4_measurement_ct1_current_Input |  | 0: OFF 1: IL1_1 2: IL2_1 3: IL3_1 |  | int | 0 | 3 | 0 | eingang.x6.1 |  |  | s | r | [9 empty] | r
_4_measurement_ct2_current_Input |  | 0: OFF 1: IL1_1 2: IL2_1 3: IL3_1 |  | int | 0 | 3 | 0 | eingang.x6.2 |  |  | s | r | [9 empty] | r
_4_measurement_ct3_current_Input |  | 0: OFF 1: IL1_1 2: IL2_1 3: IL3_1 |  | int | 0 | 3 | 0 | eingang.x6.3 |  |  | s | r | [9 empty] | r
_4_measurement_ct4_current_Input |  | 0: OFF 1: IL1_1 2: IL2_1 3: IL3_1 |  | int | 0 | 3 | 0 | eingang.x6.4 |  |  | s | r | [9 empty] | r
_4_io0_measurement_vtCircuit |  | 0 -> only measuring 1 -> U23 will be calculated 2 -> U31 will be calculated 3 -> U12 will be calculated | A | int | 0 | 3 | 0 | n.a. |  |  | s | r | [9 empty] | r
_4_measurement_vt1_primary |  |  | V | float | -100000000 | 100000000.f | 1000.f | system.schnittstellen.digital E/A DSC Port 0.vtV.primary |  |  | s | r | [9 empty] | r
_4_measurement_vt1_100Vor1000VRange |  | 0: 100V range 1: 1000V range | V | int | 0 | 1 | 1 | system.schnittstellen.digital E/A DSC Port 0.vtV.secondary |  |  | s | r | [9 empty] | r
_4_measurement_vt2_primary |  |  | V | float | -100000000 | 100000000.f | 1000.f | system.schnittstellen.digital E/A DSC Port 0.vtV.primary |  |  | s | r | [9 empty] | r
_4_measurement_vt2_100Vor1000VRange |  | 0: 100V range 1: 1000V range | V | int | 0 | 1 | 1 | system.schnittstellen.digital E/A DSC Port 0.vtV.secondary |  |  | s | r | [9 empty] | r
_4_measurement_vt3_primary |  |  | V | float | -100000000 | 100000000.f | 1000.f | system.schnittstellen.digital E/A DSC Port 0.vtV.primary |  |  | s | r | [9 empty] | r
_4_measurement_vt3_100Vor1000VRange |  | 0: 100V range 1: 1000V range | V | int | 0 | 1 | 1 | system.schnittstellen.digital E/A DSC Port 0.vtV.secondary |  |  | s | r | [9 empty] | r
_4_measurement_temperatureSensortype |  | TEMPSENSOR_NOT_USED = 0, TEMPSENSOR_MIO_KTY81 = 1, // MIO Ext. Temp KTY81-110 or -120 TEMPSENSOR_MIO_KTY84 = 2, // MIO Ext. Temp KTY84-130 TEMPSENSOR_MIO_PT1000 = 4, // MIO Ext. Temp PT1000 not in use |  | int | 0 | 3 | 0 | system.schnittstellen.digital E/A DSC Port 0.temperatur measurement (ext.) |  |  | s | r | [9 empty] | r
_4_inspector_extTempMin |  | lower boundary of the temperature measurement in the mio checkout Polarion: Project: Änderungsdienst ACF: PQAA-1598 Schutz - Externe Überwachung not in use | °C | float | -100 | 250.f | 250.f | n.a. |  |  | s | r | [9 empty] | r
_4_inspector_extTempMax |  | upper boundary of the temperature measurement in the mio checkout Polarion: Project: Änderungsdienst ACF: PQAA-1598 Schutz - Externe Überwachung not in use | °C | float | -100 | 250.f | 250.f | n.a. |  |  | s | r | [9 empty] | r
_4_inspector_LCUTempMin |  | lower boundary of the liquid cooled temperature measurement checkout Polarion: Project: Änderungsdienst ACF: PQAA-1565 Wasserkühlung not in use | °C | float | 100 | 30.f | -20 | n.a. |  |  | s | r | [9 empty] | r
_4_inspector_LCUTempMax |  | upper boundary of the liquid cooled temperature measurement checkout Polarion: Project: Änderungsdienst ACF: PQAA-1565 Wasserkühlung not in use | °C | float | 0 | 90.f | 30.f | n.a. |  |  | s | r | [9 empty] | r
#ConfigDIO
CCU_DI_1_trigger |  | 0: disabled 1: rising edge 2: falling edge |  | int | 0 | 2 | 0 |  |  |  | s | r | [9 empty] | r
CCU_DI_2_trigger |  | 0: disabled 1: rising edge 2: falling edge |  | int | 0 | 2 | 0 |  |  |  | s | r | [9 empty] | r
CCU_DI_3_trigger |  | 0: disabled 1: rising edge 2: falling edge |  | int | 0 | 2 | 0 |  |  |  | s | r | [9 empty] | r
CCU_DI_4_trigger |  | 0: disabled 1: rising edge 2: falling edge |  | int | 0 | 2 | 0 |  |  |  | s | r | [9 empty] | r
CCU_DO_1_trigger |  | 0: disabled 1: normaly open 2: normaly closed |  | int | 0 | 2 | 0 |  |  |  | s | r | [9 empty] | r
CCU_DO_2_trigger |  | 0: disabled 1: normaly open 2: normaly closed |  | int | 0 | 2 | 0 |  |  |  | s | r | [9 empty] | r
CCU_DO_3_trigger |  | 0: disabled 1: normaly open 2: normaly closed |  | int | 0 | 2 | 0 |  |  |  | s | r | [9 empty] | r
CCU_DO_4_trigger |  | 0: disabled 1: normaly open 2: normaly closed |  | int | 0 | 2 | 0 |  |  |  | s | r | [9 empty] | r
CCU_DI_1_action |  | 0: Goto PLAY 1: Goto PAUSE 2: Goto READY 3: Goto STOP 4: Toggle PLAY und STOP 5: Toggle PLAY und READY 6: Toggle PLAY und PAUSE 7: ERROR Acknowledge 8: Aktiviere Grid Following Mode 9: Aktiviere Grid Forming Mode |  | int | 0 | 9 | 0 |  |  |  | s | r | [9 empty] | r
CCU_DI_2_action |  | 0: Goto PLAY 1: Goto PAUSE 2: Goto READY 3: Goto STOP 4: Toggle PLAY und STOP 5: Toggle PLAY und READY 6: Toggle PLAY und PAUSE 7: ERROR Acknowledge 8: Aktiviere Grid Following Mode 9: Aktiviere Grid Forming Mode |  | int | 0 | 9 | 0 |  |  |  | s | r | [9 empty] | r
CCU_DI_3_action |  | 0: Goto PLAY 1: Goto PAUSE 2: Goto READY 3: Goto STOP 4: Toggle PLAY und STOP 5: Toggle PLAY und READY 6: Toggle PLAY und PAUSE 7: ERROR Acknowledge 8: Aktiviere Grid Following Mode 9: Aktiviere Grid Forming Mode |  | int | 0 | 9 | 0 |  |  |  | s | r | [9 empty] | r
CCU_DI_4_action |  | 0: Goto PLAY 1: Goto PAUSE 2: Goto READY 3: Goto STOP 4: Toggle PLAY und STOP 5: Toggle PLAY und READY 6: Toggle PLAY und PAUSE 7: ERROR Acknowledge 8: Aktiviere Grid Following Mode 9: Aktiviere Grid Forming Mode |  | int | 0 | 9 | 0 |  |  |  | s | r | [9 empty] | r
CCU_DO_1_action |  | 0: State IDLE 1: State READY 2: State RUN 3: State PAUSE 4: State ERROR 5: FRT vorgefallen 6: Grid Following oder Forming Mode aktiv 7: Grid Former synchronsiert |  | int | 0 | 7 | 0 |  |  |  | s | r | [9 empty] | r
CCU_DO_2_action |  | 0: State IDLE 1: State READY 2: State RUN 3: State PAUSE 4: State ERROR 5: FRT vorgefallen 6: Grid Following oder Forming Mode aktiv 7: Grid Former synchronsiert |  | int | 0 | 7 | 0 |  |  |  | s | r | [9 empty] | r
CCU_DO_3_action |  | 0: State IDLE 1: State READY 2: State RUN 3: State PAUSE 4: State ERROR 5: FRT vorgefallen 6: Grid Following oder Forming Mode aktiv 7: Grid Former synchronsiert |  | int | 0 | 7 | 0 |  |  |  | s | r | [9 empty] | r
CCU_DO_4_action |  | 0: State IDLE 1: State READY 2: State RUN 3: State PAUSE 4: State ERROR 5: FRT vorgefallen 6: Grid Following oder Forming Mode aktiv 7: Grid Former synchronsiert |  | int | 0 | 7 | 0 |  |  |  | s | r | [9 empty] | r
MIO_1_DI_1_trigger |  | 0: disabled 1: rising edge 2: falling edge |  | int | 0 | 2 | 1 |  |  |  | s | r | [9 empty] | r
MIO_1_DI_2_trigger |  | 0: disabled 1: rising edge 2: falling edge |  | int | 0 | 2 | 1 |  |  |  | s | r | [9 empty] | r
MIO_1_DO_1_trigger |  | 0: disabled 1: normaly open 2: normaly closed |  | int | 0 | 2 | 0 |  |  |  | s | r | [9 empty] | r
MIO_1_DO_2_trigger |  | 0: disabled 1: normaly open 2: normaly closed |  | int | 0 | 2 | 0 |  |  |  | s | r | [9 empty] | r
MIO_1_DI_1_action |  | 0: Goto PLAY 1: Goto PAUSE 2: Goto READY 3: Goto STOP 4: Toggle PLAY und STOP 5: Toggle PLAY und READY 6: Toggle PLAY und PAUSE 7: ERROR Acknowledge 8: Aktiviere Grid Following Mode 9: Aktiviere Grid Forming Mode |  | int | 0 | 9 | 0 |  |  |  | s | r | [9 empty] | r
MIO_1_DI_2_action |  | 0: Goto PLAY 1: Goto PAUSE 2: Goto READY 3: Goto STOP 4: Toggle PLAY und STOP 5: Toggle PLAY und READY 6: Toggle PLAY und PAUSE 7: ERROR Acknowledge 8: Aktiviere Grid Following Mode 9: Aktiviere Grid Forming Mode |  | int | 0 | 9 | 0 |  |  |  | s | r | [9 empty] | r
MIO_1_DO_1_action |  | 0: State IDLE 1: State READY 2: State RUN 3: State PAUSE 4: State ERROR 5: FRT vorgefallen 6: Grid Following oder Forming Mode aktiv 7: Grid Former synchronsiert |  | int | 0 | 7 | 0 |  |  |  | s | r | [9 empty] | r
MIO_1_DO_2_action |  | 0: State IDLE 1: State READY 2: State RUN 3: State PAUSE 4: State ERROR 5: FRT vorgefallen 6: Grid Following oder Forming Mode aktiv 7: Grid Former synchronsiert |  | int | 0 | 7 | 0 |  |  |  | s | r | [9 empty] | r
MIO_2_DI_1_trigger |  | 0: disabled 1: rising edge 2: falling edge |  | int | 0 | 2 | 1 |  |  |  | s | r | [9 empty] | r
MIO_2_DI_2_trigger |  | 0: disabled 1: rising edge 2: falling edge |  | int | 0 | 2 | 1 |  |  |  | s | r | [9 empty] | r
MIO_2_DO_1_trigger |  | 0: disabled 1: normaly open 2: normaly closed |  | int | 0 | 2 | 0 |  |  |  | s | r | [9 empty] | r
MIO_2_DO_2_trigger |  | 0: disabled 1: normaly open 2: normaly closed |  | int | 0 | 2 | 0 |  |  |  | s | r | [9 empty] | r
MIO_2_DI_1_action |  | 0: Goto PLAY 1: Goto PAUSE 2: Goto READY 3: Goto STOP 4: Toggle PLAY und STOP 5: Toggle PLAY und READY 6: Toggle PLAY und PAUSE 7: ERROR Acknowledge 8: Aktiviere Grid Following Mode 9: Aktiviere Grid Forming Mode |  | int | 0 | 9 | 0 |  |  |  | s | r | [9 empty] | r
MIO_2_DI_2_action |  | 0: Goto PLAY 1: Goto PAUSE 2: Goto READY 3: Goto STOP 4: Toggle PLAY und STOP 5: Toggle PLAY und READY 6: Toggle PLAY und PAUSE 7: ERROR Acknowledge 8: Aktiviere Grid Following Mode 9: Aktiviere Grid Forming Mode |  | int | 0 | 9 | 0 |  |  |  | s | r | [9 empty] | r
MIO_2_DO_1_action |  | 0: State IDLE 1: State READY 2: State RUN 3: State PAUSE 4: State ERROR 5: FRT vorgefallen 6: Grid Following oder Forming Mode aktiv 7: Grid Former synchronsiert |  | int | 0 | 7 | 0 |  |  |  | s | r | [9 empty] | r
MIO_2_DO_2_action |  | 0: State IDLE 1: State READY 2: State RUN 3: State PAUSE 4: State ERROR 5: FRT vorgefallen 6: Grid Following oder Forming Mode aktiv 7: Grid Former synchronsiert |  | int | 0 | 7 | 0 |  |  |  | s | r | [9 empty] | r
MIO_3_DI_1_trigger |  | 0: disabled 1: rising edge 2: falling edge |  | int | 0 | 2 | 1 |  |  |  | s | r | [9 empty] | r
MIO_3_DI_2_trigger |  | 0: disabled 1: rising edge 2: falling edge |  | int | 0 | 2 | 1 |  |  |  | s | r | [9 empty] | r
MIO_3_DO_1_trigger |  | 0: disabled 1: normaly open 2: normaly closed |  | int | 0 | 2 | 0 |  |  |  | s | r | [9 empty] | r
MIO_3_DO_2_trigger |  | 0: disabled 1: normaly open 2: normaly closed |  | int | 0 | 2 | 0 |  |  |  | s | r | [9 empty] | r
MIO_3_DI_1_action |  | 0: Goto PLAY 1: Goto PAUSE 2: Goto READY 3: Goto STOP 4: Toggle PLAY und STOP 5: Toggle PLAY und READY 6: Toggle PLAY und PAUSE 7: ERROR Acknowledge 8: Aktiviere Grid Following Mode 9: Aktiviere Grid Forming Mode |  | int | 0 | 9 | 0 |  |  |  | s | r | [9 empty] | r
MIO_3_DI_2_action |  | 0: Goto PLAY 1: Goto PAUSE 2: Goto READY 3: Goto STOP 4: Toggle PLAY und STOP 5: Toggle PLAY und READY 6: Toggle PLAY und PAUSE 7: ERROR Acknowledge 8: Aktiviere Grid Following Mode 9: Aktiviere Grid Forming Mode |  | int | 0 | 9 | 0 |  |  |  | s | r | [9 empty] | r
MIO_3_DO_1_action |  | 0: State IDLE 1: State READY 2: State RUN 3: State PAUSE 4: State ERROR 5: FRT vorgefallen 6: Grid Following oder Forming Mode aktiv 7: Grid Former synchronsiert |  | int | 0 | 7 | 0 |  |  |  | s | r | [9 empty] | r
MIO_3_DO_2_action |  | 0: State IDLE 1: State READY 2: State RUN 3: State PAUSE 4: State ERROR 5: FRT vorgefallen 6: Grid Following oder Forming Mode aktiv 7: Grid Former synchronsiert |  | int | 0 | 7 | 0 |  |  |  | s | r | [9 empty] | r
MIO_4_DI_1_trigger |  | 0: disabled 1: rising edge 2: falling edge |  | int | 0 | 2 | 1 |  |  |  | s | r | [9 empty] | r
MIO_4_DI_2_trigger |  | 0: disabled 1: rising edge 2: falling edge |  | int | 0 | 2 | 1 |  |  |  | s | r | [9 empty] | r
MIO_4_DO_1_trigger |  | 0: disabled 1: normaly open 2: normaly closed |  | int | 0 | 2 | 0 |  |  |  | s | r | [9 empty] | r
MIO_4_DO_2_trigger |  | 0: disabled 1: normaly open 2: normaly closed |  | int | 0 | 2 | 0 |  |  |  | s | r | [9 empty] | r
MIO_4_DI_1_action |  | 0: Goto PLAY 1: Goto PAUSE 2: Goto READY 3: Goto STOP 4: Toggle PLAY und STOP 5: Toggle PLAY und READY 6: Toggle PLAY und PAUSE 7: ERROR Acknowledge 8: Aktiviere Grid Following Mode 9: Aktiviere Grid Forming Mode |  | int | 0 | 9 | 0 |  |  |  | s | r | [9 empty] | r
MIO_4_DI_2_action |  | 0: Goto PLAY 1: Goto PAUSE 2: Goto READY 3: Goto STOP 4: Toggle PLAY und STOP 5: Toggle PLAY und READY 6: Toggle PLAY und PAUSE 7: ERROR Acknowledge 8: Aktiviere Grid Following Mode 9: Aktiviere Grid Forming Mode |  | int | 0 | 9 | 0 |  |  |  | s | r | [9 empty] | r
MIO_4_DO_1_action |  | 0: State IDLE 1: State READY 2: State RUN 3: State PAUSE 4: State ERROR 5: FRT vorgefallen 6: Grid Following oder Forming Mode aktiv 7: Grid Former synchronsiert |  | int | 0 | 7 | 0 |  |  |  | s | r | [9 empty] | r
MIO_4_DO_2_action |  | 0: State IDLE 1: State READY 2: State RUN 3: State PAUSE 4: State ERROR 5: FRT vorgefallen 6: Grid Following oder Forming Mode aktiv 7: Grid Former synchronsiert |  | int | 0 | 7 | 0 |  |  |  | s | r | [9 empty] | r
#ConfigControl
pcsControl_fundamentalCurrentLimits_positiveSequenceLimit |  | Mitsystem Grundschwingung Strombegrenzung | p.u. | float | 0.f | 1.4f | 1.4f | n.a. | yes |  | s | r | [7 empty] | r
pcsControl_fundamentalCurrentLimits_negativeSequenceLimit |  | Gegensystem Grundschwingung Strombegrenzung | p.u. | float | 0.f | 1.f | 1.f | n.a. |  |  | s | r | [7 empty] | r
pcsControl_fundamentalCurrentLimits_zeroSequenceLimit |  | Nullsystem Grundschwingung Strombegrenzung | p.u. | float | 0.f | 1.f | 0.33f | n.a. |  |  | s | r | [7 empty] | r
pcsControl_harmonicControl_vhlPositiveGainFactor |  | Harmonischen Regler Regelverstärkung |  | float | 0.001f | 1000.f | 0.1f | n.a. |  |  | s | r | [7 empty] | r
pcsControl_harmonicControl_vhlNegativeGainFactor |  | Harmonischen Regler Regelverstärkung |  | float | 0.001f | 1000.f | 0.01f | n.a. |  |  | s | r | [7 empty] | r
pcsControl_harmonicControl_adapterDroop |  |  |  | float | 0.f | 1.f | 0.01f | n.a. |  |  | s | r | [7 empty] | r
pcsControl_islandGridFormer_controlEnabled |  | Inselbetrieb Regler aktiv / wenn nicht aktiv, wird ein statischer Sinus auf der PWM gefahren. | - | int | 0 | 1 | 1 | n.a. |  |  |  | r | [7 empty] | r
pcsControl_islandGridFormer_controlGain |  | Inselbetrieb Regelverstärkung | - | float | 0.f | 1000.f | 100.f | n.a. |  |  |  | r | [7 empty] | r
pcsControl_islandGridFormer_amplitudeGain |  | Amplitudenkorrektur für externe Netzsysnchronisation | - | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r | [7 empty] | r
pcsControl_islandGridFormer_phaseOffset |  | Phasenkorrektur für externe Netzsysnchronisation | deg | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r | [7 empty] | r
pcsControl_seamlessTransfer_enabled |  | Nahtloser Übergang in den Inselbtrieb beim Einbruch der Netzspannung enable | - | int | 0 | 1 | 0 | n.a. |  |  |  | r | [7 empty] | r
pcsControl_frequencyResponse_teleControlFrequency |  | Rundsteuerfrequenz | Hz | float | 0.f | 1000.f | 0.f | System.grid.Telecontrolfrequency |  |  | s | r | s/r (optional) | [6 empty] | r
pcsControl_frequencyResponse_maxActorCurrent |  |  |  | float | 0.f | 1.f | 0.1f | n.a. |  |  | s | r | [7 empty] | r
pcsControl_frequencyResponse_maxLineVoltage |  |  |  | float | 0.f | 0.1f | 0.01f | n.a. |  |  | s | r | [7 empty] | r
pcsControl_dataProcessing_feedForwardGain |  |  |  | float | 0.001f | 1.f | 0.1f | n.a. |  |  | s | r | [7 empty] | r
pcsControl_dataProcessing_actorFLL_frequencyFilterTimeConstant |  |  |  | float | 0.f | 1.f | 0.01f | n.a. |  |  |  | r | [7 empty] | r
pcsControl_dataProcessing_actorFLL_positiveSequenceDetectorTimeConstant |  |  |  | float | 0.f | 1.f | 0.005f | n.a. |  |  |  | r | [7 empty] | r
pcsControl_dataProcessing_actorFLL_phaseDelay |  |  |  | float | -1000.f | 1000.f | 0.f | n.a. |  |  |  | r | [7 empty] | r
pcsControl_dataProcessing_lineFLL_frequencyFilterTimeConstant |  |  |  | float | 0.f | 1.f | 0.01f | n.a. |  |  |  | r | [7 empty] | r
pcsControl_dataProcessing_lineFLL_positiveSequenceDetectorTimeConstant |  |  |  | float | 0.f | 1.f | 0.005f | n.a. |  |  |  | r | [7 empty] | r
pcsControl_dataProcessing_lineFLL_phaseDelay |  |  |  | float | -1000.f | 1000.f | 0.f | n.a. |  |  |  | r | [7 empty] | r
pcsControl_dataProcessing_slowFLL_frequencyFilterTimeConstant |  |  |  | float | 0.f | 1.f | 0.1f | n.a. |  |  |  | r | [7 empty] | r
pcsControl_dataProcessing_slowFLL_positiveSequenceDetectorTimeConstant |  |  |  | float | 0.f | 1.f | 0.05f | n.a. |  |  |  | r | [7 empty] | r
pcsControl_dataProcessing_slowFLL_phaseDelay |  |  |  | float | -1000.f | 1000.f | 0.f | n.a. |  |  |  | r | [7 empty] | r
acdcConverterControl_common_dcLinkConnected |  | Sollwert der Zwischenkreisspannungsregelung wird an alle IPUs weitergegeben. |  | int | 0 | 1 | 0 | n.a. |  |  | s | r | [7 empty] | r
acdcConverterControl_common_neutralWireConnected |  | 1 = Neutralleiter ist am System angeschlossen. 0 = Neutralleiter ist nicht am System angeschlossen. |  | int | 0 | 1 | 0 | n.a. |  |  |  | r | [7 empty] | r
acdcConverterControl_derating_neutralWireLimit |  | Strombegrenzung Nullleiterstrom | p.u. | float | 0.f | 300.f | 100.f | n.a. |  |  | s | r | [7 empty] | r
acdcConverterControl_modulationIndexCalculation_zeroSequenceInjectionEnabled |  |  |  | int | 0 | 1 | 0 | n.a. | [11 empty] | r
acdcConverterControl_dcVoltageControl_setPointAdaption_Ki |  |  |  | float | 0.f | 1000.f | 100.f | n.a. |  |  | s | r | [7 empty] | r
acdcConverterControl_dcVoltageControl_setPointAdaption_modulationIndexLimit |  |  |  | float | 0.9f | 1.f | 0.98f | n.a. |  |  | s | r | [7 empty] | r
acdcConverterControl_dcVoltageControl_setPointAdaption_maxDcVoltage |  |  |  | float | 0.f | 1000.f | 950.f | n.a. |  |  | s | r | [7 empty] | r
acdcConverterControl_dcVoltageControl_control_Kp |  |  |  | float | 0.f | 1.f | 0.5 | n.a. |  |  | s | r | [7 empty] | r
acdcConverterControl_dcVoltageControl_control_Ki |  |  |  | float | 0.f | 1000.f | 5.f | n.a. |  |  | s | r | [7 empty] | r
acdcConverterControl_dcVoltageControl_control_limit |  |  |  | float | 0.f | 1000.f | 100.f | n.a. |  |  | s | r | [7 empty] | r
acdcConverterControl_acCurrentControl_voltageFeedforwardEnabled |  |  |  | int | 0 | 1 | 0 | n.a. |  |  | s | r | [7 empty] | r
acdcConverterControl_acCurrentControl_Kp |  |  |  | float | 0.f | 1.f | 0.1f | n.a. |  |  | s | r | [7 empty] | r
acdcConverterControl_acCurrentControl_Ki |  |  |  | float | 0.f | 1000.f | 100.f | n.a. |  |  | s | r | [7 empty] | r
acdcConverterControl_dcVoltageBalancing_Kp |  |  |  | float | 0.f | 1.f | 0.f | n.a. |  |  | s | r | [7 empty] | r
acdcConverterControl_dcVoltageBalancing_Ki |  |  |  | float | 0.f | 1000.f | 0.f | n.a. |  |  | s | r | [7 empty] | r
#FrequencyResponse
actorCurrentAmplitudeCorrection1 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | % | float | 0.f | 1000.f | 1.f | n.a. | yes |  |  | r |  | s | [5 empty] | r
actorCurrentAmplitudeCorrection2 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentAmplitudeCorrection3 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentAmplitudeCorrection4 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentAmplitudeCorrection5 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentAmplitudeCorrection6 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentAmplitudeCorrection7 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentAmplitudeCorrection8 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentAmplitudeCorrection9 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentAmplitudeCorrection10 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentAmplitudeCorrection11 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentAmplitudeCorrection12 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentAmplitudeCorrection13 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentAmplitudeCorrection14 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentAmplitudeCorrection15 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentAmplitudeCorrection16 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentAmplitudeCorrection17 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentAmplitudeCorrection18 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentAmplitudeCorrection19 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentAmplitudeCorrection20 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentAmplitudeCorrection21 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentAmplitudeCorrection22 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentAmplitudeCorrection23 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentAmplitudeCorrection24 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentAmplitudeCorrection25 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | Grad | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentPhaseCorrection1 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentPhaseCorrection2 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentPhaseCorrection3 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentPhaseCorrection4 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentPhaseCorrection5 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentPhaseCorrection6 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentPhaseCorrection7 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentPhaseCorrection8 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentPhaseCorrection9 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentPhaseCorrection10 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentPhaseCorrection11 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentPhaseCorrection12 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentPhaseCorrection13 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentPhaseCorrection14 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentPhaseCorrection15 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentPhaseCorrection16 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentPhaseCorrection17 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentPhaseCorrection18 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentPhaseCorrection19 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentPhaseCorrection20 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentPhaseCorrection21 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentPhaseCorrection22 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentPhaseCorrection23 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentPhaseCorrection24 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
actorCurrentPhaseCorrection25 |  | Bodediagramm Frequenzgang direkt am Anschlusspunkt ACF | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentAmplitudeCorrection1 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentAmplitudeCorrection2 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentAmplitudeCorrection3 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentAmplitudeCorrection4 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentAmplitudeCorrection5 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentAmplitudeCorrection6 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentAmplitudeCorrection7 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentAmplitudeCorrection8 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentAmplitudeCorrection9 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentAmplitudeCorrection10 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentAmplitudeCorrection11 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentAmplitudeCorrection12 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentAmplitudeCorrection13 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentAmplitudeCorrection14 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentAmplitudeCorrection15 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentAmplitudeCorrection16 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentAmplitudeCorrection17 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentAmplitudeCorrection18 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentAmplitudeCorrection19 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentAmplitudeCorrection20 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentAmplitudeCorrection21 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentAmplitudeCorrection22 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentAmplitudeCorrection23 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentAmplitudeCorrection24 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentAmplitudeCorrection25 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentPhaseCorrection1 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentPhaseCorrection2 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentPhaseCorrection3 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentPhaseCorrection4 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentPhaseCorrection5 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentPhaseCorrection6 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentPhaseCorrection7 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentPhaseCorrection8 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentPhaseCorrection9 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentPhaseCorrection10 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentPhaseCorrection11 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentPhaseCorrection12 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentPhaseCorrection13 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentPhaseCorrection14 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentPhaseCorrection15 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentPhaseCorrection16 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentPhaseCorrection17 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentPhaseCorrection18 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentPhaseCorrection19 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentPhaseCorrection20 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentPhaseCorrection21 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentPhaseCorrection22 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentPhaseCorrection23 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentPhaseCorrection24 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineCurrentPhaseCorrection25 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | Grad | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltageAmplitudeCorrection1 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltageAmplitudeCorrection2 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltageAmplitudeCorrection3 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltageAmplitudeCorrection4 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltageAmplitudeCorrection5 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltageAmplitudeCorrection6 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltageAmplitudeCorrection7 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltageAmplitudeCorrection8 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltageAmplitudeCorrection9 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltageAmplitudeCorrection10 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltageAmplitudeCorrection11 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltageAmplitudeCorrection12 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltageAmplitudeCorrection13 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltageAmplitudeCorrection14 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltageAmplitudeCorrection15 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltageAmplitudeCorrection16 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltageAmplitudeCorrection17 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltageAmplitudeCorrection18 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltageAmplitudeCorrection19 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltageAmplitudeCorrection20 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltageAmplitudeCorrection21 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltageAmplitudeCorrection22 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltageAmplitudeCorrection23 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltageAmplitudeCorrection24 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltageAmplitudeCorrection25 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | 0.f | 1000.f | 1.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltagePhaseCorrection1 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltagePhaseCorrection2 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltagePhaseCorrection3 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltagePhaseCorrection4 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltagePhaseCorrection5 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltagePhaseCorrection6 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltagePhaseCorrection7 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltagePhaseCorrection8 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltagePhaseCorrection9 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltagePhaseCorrection10 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltagePhaseCorrection11 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltagePhaseCorrection12 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltagePhaseCorrection13 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltagePhaseCorrection14 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltagePhaseCorrection15 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltagePhaseCorrection16 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltagePhaseCorrection17 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltagePhaseCorrection18 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltagePhaseCorrection19 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltagePhaseCorrection20 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltagePhaseCorrection21 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltagePhaseCorrection22 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltagePhaseCorrection23 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltagePhaseCorrection24 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
lineVoltagePhaseCorrection25 |  | Bodediagramm Frequenzgang direkt am MIO Messpunkt | % | float | -360.f | 360.f | 0.f | n.a. |  |  |  | r |  | s | [5 empty] | r
#ConfigGridConBackend
eth0_ip |  |  |  | string | 0.0.0.0 | 255.255.255.255 | 10.0.1.2 | n.a. |  |  | s | r
eth0_netmask |  | network prefix length |  | int | 0 | 31 | 24 | n.a. |  |  | s | r
eth0_gateway |  |  |  | string | 0.0.0.0 | 255.255.255.255 | 10.0.1.254 | n.a. |  |  | s | r
eth0_macAddress |  |  |  | string | no boundaries |  |  | n.a. |  |  | s | r
eth0_config |  | dhcp or static |  | string |  |  | static | n.a. |  |  | s | r
eth1_ip |  |  |  | string | 0.0.0.0 | 255.255.255.255 | 10.0.0.2 | n.a. |  |  | s | r
eth1_netmask |  | network prefix length |  | int | 0 | 31 | 24 | n.a. … fun fact |  |  | s | r
eth1_gateway |  |  |  | string | 0.0.0.0 | 255.255.255.255 | 10.0.0.254 | n.a. … fun fact |  |  | s | r
eth1_macAddress |  |  |  | string | no boundaries |  |  | system.schnittstellen.ethernet.MAC-Adresse |  |  | s | r
eth1_config |  | dhcp or static |  | string |  |  | static | n.a. |  |  | s | r
hmi_brigthness |  |  |  | int | 0 | 4 | 0 | n.a. … fun fact |  |  | s | r
hmi_ScreenSaver |  |  |  | int | 0 | 4 | 0 | n.a. … fun fact |  |  | s | r
#ConfigModbus
general_modbusenabled |  | Matevz und Tobias fragen |  | values ccu2 and ccu1 equal? |  |  |  | n.a. | no |  | s | r | s/r (optional)
general_monitorConnectionState |  |  |  | s.o. |  |  |  | n.a. |  |  | s | r | s/r (optional)
general_monitorLifebit |  |  |  | s.o. |  |  |  | n.a. |  |  | s | r | s/r (optional)
modbus_tcp_ipaddress |  |  |  | s.o. |  |  |  | n.a. |  |  | s | r | s/r (optional)
modbus_tcp_subnetmask |  |  |  | s.o. |  |  |  | n.a. |  |  | s | r | s/r (optional)
modbus_tcp_gateway |  |  |  | s.o. |  |  |  | n.a. |  |  | s | r | s/r (optional)
modbus_tcp_dhcpon |  |  |  | s.o. |  |  |  | n.a. |  |  | s | r | s/r (optional)
modbus_tcp_duplexmode |  |  |  | s.o. |  |  |  | n.a. |  |  | s | r | s/r (optional)
modbus_tcp_timeout |  |  |  | s.o. |  |  |  | n.a. |  |  | s | r | s/r (optional)
modbus_tcp_processtimeout |  |  |  | s.o. |  |  |  | n.a. |  |  | s | r | s/r (optional)
#ConfigGridcode
gridCodeSelector |  | 0: custom setting via database 1: VDE-AR-N 4105 2: VDE-AR-N 4110 3: EN 50549-2 |  | int | 0 | 3 | 0 | n.a. | no |  | s | r | [7 empty] | r
faultDetection_voltage_enable |  | enable/disable the detection for voltage |  | int | 0 | 1 | 0 | n.a. |  |  | s | r |  | yes | yes | yes | r |  |  | r
faultDetection_voltage_timeOut |  | time out for voltage frt |  | int | 0 | 3600 | 0 | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_lowRideThroughEntryLevel |  | lower entry level for voltage |  | float | 0.f | 1.f | 0.f | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_lowRideThroughExitLevel |  | lower exit level for voltage |  | float | 0.f | 1.f | 0.f | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_highRideThroughEntryLevel |  | upper entry level for voltage |  | float | 1.f | 2.f | 2.f | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_highRideThroughExitLevel |  | upper exit level for voltage |  | float | 1.f | 2.f | 2.f | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_lowRideThroughTimeVector1 |  | time coordinate 1 for low voltage |  | int | 0 | 3600 | 0 | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_lowRideThroughTimeVector2 |  | time coordinate 2 for low voltage |  | int | 0 | 3600 | 0 | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_lowRideThroughTimeVector3 |  | time coordinate 3 for low voltage |  | int | 0 | 3600 | 0 | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_lowRideThroughTimeVector4 |  | time coordinate 4 for low voltage |  | int | 0 | 3600 | 0 | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_lowRideThroughTimeVector5 |  | time coordinate 5 for low voltage |  | int | 0 | 3600 | 0 | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_lowRideThroughTimeVector6 |  | time coordinate 6 for low voltage |  | int | 0 | 3600 | 0 | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_lowRideThroughTimeVector7 |  | time coordinate 7 for low voltage |  | int | 0 | 3600 | 0 | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_lowRideThroughValueVector1 |  | reference value coordinate 1 for low voltage |  | float | 0.f | 1.f | 0.f | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_lowRideThroughValueVector2 |  | reference value coordinate 2 for low voltage |  | float | 0.f | 1.f | 0.f | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_lowRideThroughValueVector3 |  | reference value coordinate 3 for low voltage |  | float | 0.f | 1.f | 0.f | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_lowRideThroughValueVector4 |  | reference value coordinate 4 for low voltage |  | float | 0.f | 1.f | 0.f | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_lowRideThroughValueVector5 |  | reference value coordinate 5 for low voltage |  | float | 0.f | 1.f | 0.f | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_lowRideThroughValueVector6 |  | reference value coordinate 6 for low voltage |  | float | 0.f | 1.f | 0.f | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_lowRideThroughValueVector7 |  | reference value coordinate 7 for low voltage |  | float | 0.f | 1.f | 0.f | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_highRideThroughTimeVector1 |  | time coordinate 1 for high voltage |  | int | 0 | 3600 | 0 | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_highRideThroughTimeVector2 |  | time coordinate 2 for high voltage |  | int | 0 | 3600 | 0 | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_highRideThroughTimeVector3 |  | time coordinate 3 for high voltage |  | int | 0 | 3600 | 0 | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_highRideThroughTimeVector4 |  | time coordinate 4 for high voltage |  | int | 0 | 3600 | 0 | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_highRideThroughTimeVector5 |  | time coordinate 5 for high voltage |  | int | 0 | 3600 | 0 | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_highRideThroughTimeVector6 |  | time coordinate 6 for high voltage |  | int | 0 | 3600 | 0 | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_highRideThroughTimeVector7 |  | time coordinate 7 for high voltage |  | int | 0 | 3600 | 0 | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_highRideThroughValueVector1 |  | reference value coordinate 1 for high voltage |  | float | 1.f | 2.f | 2.f | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_highRideThroughValueVector2 |  | reference value coordinate 2 for high voltage |  | float | 1.f | 2.f | 2.f | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_highRideThroughValueVector3 |  | reference value coordinate 3 for high voltage |  | float | 1.f | 2.f | 2.f | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_highRideThroughValueVector4 |  | reference value coordinate 4 for high voltage |  | float | 1.f | 2.f | 2.f | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_highRideThroughValueVector5 |  | reference value coordinate 5 for high voltage |  | float | 1.f | 2.f | 2.f | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_highRideThroughValueVector6 |  | reference value coordinate 6 for high voltage |  | float | 1.f | 2.f | 2.f | n.a. |  |  | s | r | [7 empty] | r
faultDetection_voltage_highRideThroughValueVector7 |  | reference value coordinate 7 for high voltage |  | float | 1.f | 2.f | 2.f | n.a. |  |  | s | r | [7 empty] | r
faultDetection_frequency_upperLimit |  | level for permanent under frequency |  | float | 1.f | 2.f | 2.f | n.a. |  |  | s | r | [7 empty] | r
faultDetection_frequency_upperCriticalLimit |  | level for limited under frequency |  | float | 1.f | 2.f | 2.f | n.a. |  |  | s | r | [7 empty] | r
faultDetection_frequency_upperErrorLimit |  | level for under frequency fault |  | float | 1.f | 2.f | 2.f | n.a. |  |  | s | r | [7 empty] | r
faultDetection_frequency_upperCriticalTimeOut |  | time out for limited under frequency |  | int | 0 | 7200 | 7200 | n.a. |  |  | s | r | [7 empty] | r
faultDetection_frequency_lowerLimit |  | level for permanent over frequency |  | float | 0.f | 1.f | 0.f | n.a. |  |  | s | r | [7 empty] | r
faultDetection_frequency_lowerCriticalLimit |  | level for limited over frequency |  | float | 0.f | 1.f | 0.f | n.a. |  |  | s | r | [7 empty] | r
faultDetection_frequency_lowerErrorLimit |  | level for over frequency fault |  | float | 0.f | 1.f | 0.f | n.a. |  |  | s | r | [7 empty] | r
faultDetection_frequency_lowerCriticalTimeOut |  | time out for limited over frequency |  | int | 0 | 7200 | 7200 | n.a. |  |  | s | r | [7 empty] | r
faultControl_voltage_enable |  |  |  | int | 0 | 1 | 0 | n.a. |  |  | s | r | [7 empty] | r
faultControl_frequency_enable |  |  |  | int | 0 | 1 | 0 | n.a. |  |  | s | r | [7 empty] | r
faultControl_voltage_kFactor |  |  |  | float | 0.f | 100.f | 0.f | n.a. |  |  | s | r | [7 empty] | r
faultControl_frequency_kFactor |  |  |  | float | 0.f | 100.f | 0.f | n.a. |  |  | s | r | [7 empty] | r
faultControl_voltage_zeroOutputVoltageLevel |  |  |  | float | 0.f | 1.f | 0.f | n.a. |  |  | s | r | [7 empty] | r
syncConditionCheck_connection_lower_voltage_level |  | lower voltage level for connection after fault |  | float | 0.f | 1.f | 0.f | n.a. |  |  | s | r |  |  |  | r
syncConditionCheck_connection_upper_voltage_level |  | upper voltage level for connection after fault |  | float | 1.f | 2.f | 2.f | n.a. |  |  | s | r |  |  |  | r
syncConditionCheck_connection_lower_frequency_level |  | lower frequency level for connection after fault |  | float | 0.f | 1.f | 0.f | n.a. |  |  | s | r | [7 empty] | r
syncConditionCheck_connection_upper_frequency_level |  | upper frequency level for connection after fault |  | float | 1.f | 2.f | 2.f | n.a. |  |  | s | r | [7 empty] | r
syncConditionCheck_connection_observation_time |  | duration of the observation for connection after fault |  | int | 0 | 3600 | 0.f | n.a. |  |  | s | r |  |  |  |  | r
activePowerRateLimiter_connectionAfterFaultChangeRate |  |  |  | float | 0.f | 10.f | 0.f | n.a. |  |  | s | r | [7 empty] | r
activePowerRateLimiter_connectionAfterFaultDuration |  |  |  | int | 0 | 3600 | 0 | n.a. |  |  | s | r | [7 empty] | r
activePowerRateLimiter_frequencyFrtChangeRate |  |  |  | float | 0.f | 10.f | 0.f | n.a. |  |  | s | r | [7 empty] | r
activePowerRateLimiter_frequencyFrtDuration |  |  |  | int | 0 | 3600 | 0 | n.a. |  |  | s | r | [7 empty] | r
#lastRowOfSheet
general_modbusenabled |  |  |  | values ccu2 and ccu1 equal? |  |  |  | n.a. | no |  | s | r | s/r (optional)
general_monitorConnectionState |  |  |  | s.o. |  |  |  | n.a. |  |  | s | r | s/r (optional)
general_monitorLifebit |  |  |  | s.o. |  |  |  | n.a. |  |  | s | r | s/r (optional)
modbus_tcp_ipaddress |  |  |  | s.o. |  |  |  | n.a. |  |  | s | r | s/r (optional)
modbus_tcp_subnetmask |  |  |  | s.o. |  |  |  | n.a. |  |  | s | r | s/r (optional)
modbus_tcp_gateway |  |  |  | s.o. |  |  |  | n.a. |  |  | s | r | s/r (optional)
modbus_tcp_dhcpon |  |  |  | s.o. |  |  |  | n.a. |  |  | s | r | s/r (optional)
modbus_tcp_duplexmode |  |  |  | s.o. |  |  |  | n.a. |  |  | s | r | s/r (optional)
modbus_tcp_timeout |  |  |  | s.o. |  |  |  | n.a. |  |  | s | r | s/r (optional)
modbus_tcp_processtimeout |  |  |  | s.o. |  |  |  | n.a. |  |  | s | r | s/r (optional)

## DSCInfo
#name | #description | #datatype | #unit | Page on HMI ( " ." means subpage ) | Send to R5
versionhistory: see below at the bottom of sheet | [5 empty] | Prozessor: | A53 | [7 empty] | R5
[6 empty] | Layer: | DataLayer | PresentationLayer |  | BusinessLayer |  |  |  | HW- middlewarelayer (name not decided yet) | ConfigurationLayer | BusinessLayer | HW-MiddlewareLayer
[6 empty] | Module: | DataBase | grid ConBackend [optional = if page requested] | anybus [optional = if page requested] | ErrorHandler | Logger | Measurements | Statemachine | DSCLib | module is not planned yet | Control | Actor | Mio | DSCLib
#DSC_Info
DSCPort0_flashBlock_boardRevision | Firmware Information Board Revision | unsigned int
DSCPort0_flashBlock_characteristic | Firmware Information Characteristic 0:=MIO3V4C / 1:=MIO3V3C | unsigned int
DSCPort0_flashBlock_deviceClass | Firmware Information Device Class 0:=IPU / 1:=MIO | unsigned int
DSCPort0_flashBlock_deviceType | Firmware Information Device Type | unsigned int
DSCPort0_flashBlock_readSuccess | true (1), wenn das Auslesen der Flashinformation erfolgreich war, false (0) wenn das Auslesen der Flash Informationen nicht erfolgreich war. | unsigned int
DSCPort0_flashBlock_revisionData | Firmware Information Revision siehe auch PQ16I1-1788 - DSC Client Flashblock | unsigned int
DSCPort0_infoBlock_articlenumber | Artikelnummer des DSC Clients | unsigned int
DSCPort0_infoBlock_bugfix | DSC Client Firmware Bugfixnummer | unsigned int
DSCPort0_infoBlock_ident1 | DSC Client InfoBlock Ident 1 | unsigned int
DSCPort0_infoBlock_ident2 | DSC Client InfoBlock Ident 2 | unsigned int
DSCPort0_infoBlock_description | DSC Client InfoBlock description | unsigned int
DSCPort0_infoBlock_reserved | DSC Client InfoBlock Reserved | unsigned int
DSCPort0_infoBlock_revision | DSC Client Firmware Revisionsnummer | unsigned int
DSCPort0_infoBlock_success | true (1), wenn das Auslesen der Flashinformation erfolgreich war, false (0) wenn das Auslesen der Flash Informationen nicht erfolgreich war. PQ16I1-1783 - DSC Client Infoblock | unsigned int
DSCPort1_flashBlock_boardRevision | Firmware Information Board Revision | unsigned int
DSCPort1_flashBlock_characteristic | Firmware Information Characteristic 0:=MIO3V4C / 1:=MIO3V3C | unsigned int
DSCPort1_flashBlock_deviceClass | Firmware Information Device Class 0:=IPU / 1:=MIO | unsigned int
DSCPort1_flashBlock_deviceType | Firmware Information Device Type | unsigned int
DSCPort1_flashBlock_readSuccess | true (1), wenn das Auslesen der Flashinformation erfolgreich war, false (0) wenn das Auslesen der Flash Informationen nicht erfolgreich war. | unsigned int
DSCPort1_flashBlock_revisionData | Firmware Information Revision siehe auch PQ16I1-1788 - DSC Client Flashblock | unsigned int
DSCPort1_infoBlock_articlenumber | Artikelnummer des DSC Clients | unsigned int
DSCPort1_infoBlock_bugfix | DSC Client Firmware Bugfixnummer | unsigned int
DSCPort1_infoBlock_ident1 | DSC Client InfoBlock Ident 1 | unsigned int
DSCPort1_infoBlock_ident2 | DSC Client InfoBlock Ident 2 | unsigned int
DSCPort1_infoBlock_description | DSC Client InfoBlock description | unsigned int
DSCPort1_infoBlock_reserved | DSC Client InfoBlock Reserved | unsigned int
DSCPort1_infoBlock_revision | DSC Client Firmware Revisionsnummer | unsigned int
DSCPort1_infoBlock_success | true (1), wenn das Auslesen der Flashinformation erfolgreich war, false (0) wenn das Auslesen der Flash Informationen nicht erfolgreich war. PQ16I1-1783 - DSC Client Infoblock | unsigned int
DSCPort2_flashBlock_boardRevision | Firmware Information Board Revision | unsigned int
DSCPort2_flashBlock_characteristic | Firmware Information Characteristic 0:=MIO3V4C / 1:=MIO3V3C | unsigned int
DSCPort2_flashBlock_deviceClass | Firmware Information Device Class 0:=IPU / 1:=MIO | unsigned int
DSCPort2_flashBlock_deviceType | Firmware Information Device Type | unsigned int
DSCPort2_flashBlock_readSuccess | true (1), wenn das Auslesen der Flashinformation erfolgreich war, false (0) wenn das Auslesen der Flash Informationen nicht erfolgreich war. | unsigned int
DSCPort2_flashBlock_revisionData | Firmware Information Revision siehe auch PQ16I1-1788 - DSC Client Flashblock | unsigned int
DSCPort2_infoBlock_articlenumber | Artikelnummer des DSC Clients | unsigned int
DSCPort2_infoBlock_bugfix | DSC Client Firmware Bugfixnummer | unsigned int
DSCPort2_infoBlock_ident1 | DSC Client InfoBlock Ident 1 | unsigned int
DSCPort2_infoBlock_ident2 | DSC Client InfoBlock Ident 2 | unsigned int
DSCPort2_infoBlock_description | DSC Client InfoBlock description | unsigned int
DSCPort2_infoBlock_reserved | DSC Client InfoBlock Reserved | unsigned int
DSCPort2_infoBlock_revision | DSC Client Firmware Revisionsnummer | unsigned int
DSCPort2_infoBlock_success | true (1), wenn das Auslesen der Flashinformation erfolgreich war, false (0) wenn das Auslesen der Flash Informationen nicht erfolgreich war. PQ16I1-1783 - DSC Client Infoblock | unsigned int
DSCPort3_flashBlock_boardRevision | Firmware Information Board Revision | unsigned int
DSCPort3_flashBlock_characteristic | Firmware Information Characteristic 0:=MIO3V4C / 1:=MIO3V3C | unsigned int
DSCPort3_flashBlock_deviceClass | Firmware Information Device Class 0:=IPU / 1:=MIO | unsigned int
DSCPort3_flashBlock_deviceType | Firmware Information Device Type | unsigned int
DSCPort3_flashBlock_readSuccess | true (1), wenn das Auslesen der Flashinformation erfolgreich war, false (0) wenn das Auslesen der Flash Informationen nicht erfolgreich war. | unsigned int
DSCPort3_flashBlock_revisionData | Firmware Information Revision siehe auch PQ16I1-1788 - DSC Client Flashblock | unsigned int
DSCPort3_infoBlock_articlenumber | Artikelnummer des DSC Clients | unsigned int
DSCPort3_infoBlock_bugfix | DSC Client Firmware Bugfixnummer | unsigned int
DSCPort3_infoBlock_ident1 | DSC Client InfoBlock Ident 1 | unsigned int
DSCPort3_infoBlock_ident2 | DSC Client InfoBlock Ident 2 | unsigned int
DSCPort3_infoBlock_description | DSC Client InfoBlock description | unsigned int
DSCPort3_infoBlock_reserved | DSC Client InfoBlock Reserved | unsigned int
DSCPort3_infoBlock_revision | DSC Client Firmware Revisionsnummer | unsigned int
DSCPort3_infoBlock_success | true (1), wenn das Auslesen der Flashinformation erfolgreich war, false (0) wenn das Auslesen der Flash Informationen nicht erfolgreich war. PQ16I1-1783 - DSC Client Infoblock | unsigned int
DSCPort4_flashBlock_boardRevision | Firmware Information Board Revision | unsigned int
DSCPort4_flashBlock_characteristic | Firmware Information Characteristic 0:=MIO3V4C / 1:=MIO3V3C | unsigned int
DSCPort4_flashBlock_deviceClass | Firmware Information Device Class 0:=IPU / 1:=MIO | unsigned int
DSCPort4_flashBlock_deviceType | Firmware Information Device Type | unsigned int
DSCPort4_flashBlock_readSuccess | true (1), wenn das Auslesen der Flashinformation erfolgreich war, false (0) wenn das Auslesen der Flash Informationen nicht erfolgreich war. | unsigned int
DSCPort4_flashBlock_revisionData | Firmware Information Revision siehe auch PQ16I1-1788 - DSC Client Flashblock | unsigned int
DSCPort4_infoBlock_articlenumber | Artikelnummer des DSC Clients | unsigned int
DSCPort4_infoBlock_bugfix | DSC Client Firmware Bugfixnummer | unsigned int
DSCPort4_infoBlock_ident1 | DSC Client InfoBlock Ident 1 | unsigned int
DSCPort4_infoBlock_ident2 | DSC Client InfoBlock Ident 2 | unsigned int
DSCPort4_infoBlock_description | DSC Client InfoBlock description | unsigned int
DSCPort4_infoBlock_reserved | DSC Client InfoBlock Reserved | unsigned int
DSCPort4_infoBlock_revision | DSC Client Firmware Revisionsnummer | unsigned int
DSCPort4_infoBlock_success | true (1), wenn das Auslesen der Flashinformation erfolgreich war, false (0) wenn das Auslesen der Flash Informationen nicht erfolgreich war. PQ16I1-1783 - DSC Client Infoblock | unsigned int
DSCPort5_flashBlock_boardRevision | Firmware Information Board Revision | unsigned int
DSCPort5_flashBlock_characteristic | Firmware Information Characteristic 0:=MIO3V4C / 1:=MIO3V3C | unsigned int
DSCPort5_flashBlock_deviceClass | Firmware Information Device Class 0:=IPU / 1:=MIO | unsigned int
DSCPort5_flashBlock_deviceType | Firmware Information Device Type | unsigned int
DSCPort5_flashBlock_readSuccess | true (1), wenn das Auslesen der Flashinformation erfolgreich war, false (0) wenn das Auslesen der Flash Informationen nicht erfolgreich war. | unsigned int
DSCPort5_flashBlock_revisionData | Firmware Information Revision siehe auch PQ16I1-1788 - DSC Client Flashblock | unsigned int
DSCPort5_infoBlock_articlenumber | Artikelnummer des DSC Clients | unsigned int
DSCPort5_infoBlock_bugfix | DSC Client Firmware Bugfixnummer | unsigned int
DSCPort5_infoBlock_ident1 | DSC Client InfoBlock Ident 1 | unsigned int
DSCPort5_infoBlock_ident2 | DSC Client InfoBlock Ident 2 | unsigned int
DSCPort5_infoBlock_description | DSC Client InfoBlock description | unsigned int
DSCPort5_infoBlock_reserved | DSC Client InfoBlock Reserved | unsigned int
DSCPort5_infoBlock_revision | DSC Client Firmware Revisionsnummer | unsigned int
DSCPort5_infoBlock_success | true (1), wenn das Auslesen der Flashinformation erfolgreich war, false (0) wenn das Auslesen der Flash Informationen nicht erfolgreich war. PQ16I1-1783 - DSC Client Infoblock | unsigned int
DSCPort6_flashBlock_boardRevision | Firmware Information Board Revision | unsigned int
DSCPort6_flashBlock_characteristic | Firmware Information Characteristic 0:=MIO3V4C / 1:=MIO3V3C | unsigned int
DSCPort6_flashBlock_deviceClass | Firmware Information Device Class 0:=IPU / 1:=MIO | unsigned int
DSCPort6_flashBlock_deviceType | Firmware Information Device Type | unsigned int
DSCPort6_flashBlock_readSuccess | true (1), wenn das Auslesen der Flashinformation erfolgreich war, false (0) wenn das Auslesen der Flash Informationen nicht erfolgreich war. | unsigned int
DSCPort6_flashBlock_revisionData | Firmware Information Revision siehe auch PQ16I1-1788 - DSC Client Flashblock | unsigned int
DSCPort6_infoBlock_articlenumber | Artikelnummer des DSC Clients | unsigned int
DSCPort6_infoBlock_bugfix | DSC Client Firmware Bugfixnummer | unsigned int
DSCPort6_infoBlock_ident1 | DSC Client InfoBlock Ident 1 | unsigned int
DSCPort6_infoBlock_ident2 | DSC Client InfoBlock Ident 2 | unsigned int
DSCPort6_infoBlock_description | DSC Client InfoBlock description | unsigned int
DSCPort6_infoBlock_reserved | DSC Client InfoBlock Reserved | unsigned int
DSCPort6_infoBlock_revision | DSC Client Firmware Revisionsnummer | unsigned int
DSCPort6_infoBlock_success | true (1), wenn das Auslesen der Flashinformation erfolgreich war, false (0) wenn das Auslesen der Flash Informationen nicht erfolgreich war. PQ16I1-1783 - DSC Client Infoblock | unsigned int
DSCPort7_flashBlock_boardRevision | Firmware Information Board Revision | unsigned int
DSCPort7_flashBlock_characteristic | Firmware Information Characteristic 0:=MIO3V4C / 1:=MIO3V3C | unsigned int
DSCPort7_flashBlock_deviceClass | Firmware Information Device Class 0:=IPU / 1:=MIO | unsigned int
DSCPort7_flashBlock_deviceType | Firmware Information Device Type | unsigned int
DSCPort7_flashBlock_readSuccess | true (1), wenn das Auslesen der Flashinformation erfolgreich war, false (0) wenn das Auslesen der Flash Informationen nicht erfolgreich war. | unsigned int
DSCPort7_flashBlock_revisionData | Firmware Information Revision siehe auch PQ16I1-1788 - DSC Client Flashblock | unsigned int
DSCPort7_infoBlock_articlenumber | Artikelnummer des DSC Clients | unsigned int
DSCPort7_infoBlock_bugfix | DSC Client Firmware Bugfixnummer | unsigned int
DSCPort7_infoBlock_ident1 | DSC Client InfoBlock Ident 1 | unsigned int
DSCPort7_infoBlock_ident2 | DSC Client InfoBlock Ident 2 | unsigned int
DSCPort7_infoBlock_description | DSC Client InfoBlock description | unsigned int
DSCPort7_infoBlock_reserved | DSC Client InfoBlock Reserved | unsigned int
DSCPort7_infoBlock_revision | DSC Client Firmware Revisionsnummer | unsigned int
DSCPort7_infoBlock_success | true (1), wenn das Auslesen der Flashinformation erfolgreich war, false (0) wenn das Auslesen der Flash Informationen nicht erfolgreich war. PQ16I1-1783 - DSC Client Infoblock | unsigned int
DSCPort8_flashBlock_boardRevision | Firmware Information Board Revision | unsigned int
DSCPort8_flashBlock_characteristic | Firmware Information Characteristic 0:=MIO3V4C / 1:=MIO3V3C | unsigned int
DSCPort8_flashBlock_deviceClass | Firmware Information Device Class 0:=IPU / 1:=MIO | unsigned int
DSCPort8_flashBlock_deviceType | Firmware Information Device Type | unsigned int
DSCPort8_flashBlock_readSuccess | true (1), wenn das Auslesen der Flashinformation erfolgreich war, false (0) wenn das Auslesen der Flash Informationen nicht erfolgreich war. | unsigned int
DSCPort8_flashBlock_revisionData | Firmware Information Revision siehe auch PQ16I1-1788 - DSC Client Flashblock | unsigned int
DSCPort8_infoBlock_articlenumber | Artikelnummer des DSC Clients | unsigned int
DSCPort8_infoBlock_bugfix | DSC Client Firmware Bugfixnummer | unsigned int
DSCPort8_infoBlock_ident1 | DSC Client InfoBlock Ident 1 | unsigned int
DSCPort8_infoBlock_ident2 | DSC Client InfoBlock Ident 1 | unsigned int
DSCPort8_infoBlock_description | DSC Client InfoBlock description | unsigned int
DSCPort8_infoBlock_reserved | DSC Client InfoBlock Reserved | unsigned int
DSCPort8_infoBlock_revision | DSC Client Firmware Revisionsnummer | unsigned int
DSCPort8_infoBlock_success | true (1), wenn das Auslesen der Flashinformation erfolgreich war, false (0) wenn das Auslesen der Flash Informationen nicht erfolgreich war. PQ16I1-1783 - DSC Client Infoblock | unsigned int
DSCPort9_flashBlock_boardRevision | Firmware Information Board Revision | unsigned int
DSCPort9_flashBlock_characteristic | Firmware Information Characteristic 0:=MIO3V4C / 1:=MIO3V3C | unsigned int
DSCPort9_flashBlock_deviceClass | Firmware Information Device Class 0:=IPU / 1:=MIO | unsigned int
DSCPort9_flashBlock_deviceType | Firmware Information Device Type | unsigned int
DSCPort9_flashBlock_readSuccess | true (1), wenn das Auslesen der Flashinformation erfolgreich war, false (0) wenn das Auslesen der Flash Informationen nicht erfolgreich war. | unsigned int
DSCPort9_flashBlock_revisionData | Firmware Information Revision siehe auch PQ16I1-1788 - DSC Client Flashblock | unsigned int
DSCPort9_infoBlock_articlenumber | Artikelnummer des DSC Clients | unsigned int
DSCPort9_infoBlock_bugfix | DSC Client Firmware Bugfixnummer | unsigned int
DSCPort9_infoBlock_ident1 | DSC Client InfoBlock Ident 1 | unsigned int
DSCPort9_infoBlock_ident2 | DSC Client InfoBlock Ident 2 | unsigned int
DSCPort9_infoBlock_description | DSC Client InfoBlock description | unsigned int
DSCPort9_infoBlock_reserved | DSC Client InfoBlock Reserved | unsigned int
DSCPort9_infoBlock_revision | DSC Client Firmware Revisionsnummer | unsigned int
DSCPort9_infoBlock_success | true (1), wenn das Auslesen der Flashinformation erfolgreich war, false (0) wenn das Auslesen der Flash Informationen nicht erfolgreich war. PQ16I1-1783 - DSC Client Infoblock | unsigned int
DSCPort10_flashBlock_boardRevision | Firmware Information Board Revision | unsigned int
DSCPort10_flashBlock_characteristic | Firmware Information Characteristic 0:=MIO3V4C / 1:=MIO3V3C | unsigned int
DSCPort10_flashBlock_deviceClass | Firmware Information Device Class 0:=IPU / 1:=MIO | unsigned int
DSCPort10_flashBlock_deviceType | Firmware Information Device Type | unsigned int
DSCPort10_flashBlock_readSuccess | true (1), wenn das Auslesen der Flashinformation erfolgreich war, false (0) wenn das Auslesen der Flash Informationen nicht erfolgreich war. | unsigned int
DSCPort10_flashBlock_revisionData | Firmware Information Revision siehe auch PQ16I1-1788 - DSC Client Flashblock | unsigned int
DSCPort10_infoBlock_articlenumber | Artikelnummer des DSC Clients | unsigned int
DSCPort10_infoBlock_bugfix | DSC Client Firmware Bugfixnummer | unsigned int
DSCPort10_infoBlock_ident1 | DSC Client InfoBlock Ident 1 | unsigned int
DSCPort10_infoBlock_ident2 | DSC Client InfoBlock Ident 2 | unsigned int
DSCPort10_infoBlock_description | DSC Client InfoBlock description | unsigned int
DSCPort10_infoBlock_reserved | DSC Client InfoBlock Reserved | unsigned int
DSCPort10_infoBlock_revision | DSC Client Firmware Revisionsnummer | unsigned int
DSCPort10_infoBlock_success | true (1), wenn das Auslesen der Flashinformation erfolgreich war, false (0) wenn das Auslesen der Flash Informationen nicht erfolgreich war. PQ16I1-1783 - DSC Client Infoblock | unsigned int
DSCPort11_flashBlock_boardRevision | Firmware Information Board Revision | unsigned int
DSCPort11_flashBlock_characteristic | Firmware Information Characteristic 0:=MIO3V4C / 1:=MIO3V3C | unsigned int
DSCPort11_flashBlock_deviceClass | Firmware Information Device Class 0:=IPU / 1:=MIO | unsigned int
DSCPort11_flashBlock_deviceType | Firmware Information Device Type | unsigned int
DSCPort11_flashBlock_readSuccess | true (1), wenn das Auslesen der Flashinformation erfolgreich war, false (0) wenn das Auslesen der Flash Informationen nicht erfolgreich war. | unsigned int
DSCPort11_flashBlock_revisionData | Firmware Information Revision siehe auch PQ16I1-1788 - DSC Client Flashblock | unsigned int
DSCPort11_infoBlock_articlenumber | Artikelnummer des DSC Clients | unsigned int
DSCPort11_infoBlock_bugfix | DSC Client Firmware Bugfixnummer | unsigned int
DSCPort11_infoBlock_ident1 | DSC Client InfoBlock Ident 1 | unsigned int
DSCPort11_infoBlock_ident2 | DSC Client InfoBlock Ident 2 | unsigned int
DSCPort11_infoBlock_description | DSC Client InfoBlock description | unsigned int
DSCPort11_infoBlock_reserved | DSC Client InfoBlock Reserved | unsigned int
DSCPort11_infoBlock_revision | DSC Client Firmware Revisionsnummer | unsigned int
DSCPort11_infoBlock_success | true (1), wenn das Auslesen der Flashinformation erfolgreich war, false (0) wenn das Auslesen der Flash Informationen nicht erfolgreich war. PQ16I1-1783 - DSC Client Infoblock | unsigned int
DSCPort0_C1_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort0_C1_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort0_C1_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort0_C2_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort0_C2_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort0_C2_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort0_C3_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort0_C3_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort0_C3_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort0_C1_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort0_C1_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort0_C1_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort0_C2_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort0_C2_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort0_C2_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort0_C3_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort0_C3_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort0_C3_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort0_V1_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort0_V1_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort0_V1_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort0_V2_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort0_V2_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort0_V2_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort0_V3_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort0_V3_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort0_V3_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort0_V1_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort0_V1_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort0_V1_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort0_V2_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort0_V2_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort0_V2_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort0_V3_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort0_V3_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort0_V3_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort1_C1_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort1_C1_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort1_C1_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort1_C2_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort1_C2_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort1_C2_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort1_C3_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort1_C3_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort1_C3_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort1_C1_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort1_C1_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort1_C1_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort1_C2_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort1_C2_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort1_C2_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort1_C3_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort1_C3_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort1_C3_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort1_V1_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort1_V1_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort1_V1_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort1_V2_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort1_V2_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort1_V2_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort1_V3_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort1_V3_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort1_V3_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort1_V1_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort1_V1_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort1_V1_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort1_V2_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort1_V2_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort1_V2_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort1_V3_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort1_V3_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort1_V3_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort2_C1_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort2_C1_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort2_C1_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort2_C2_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort2_C2_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort2_C2_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort2_C3_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort2_C3_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort2_C3_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort2_C1_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort2_C1_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort2_C1_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort2_C2_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort2_C2_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort2_C2_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort2_C3_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort2_C3_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort2_C3_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort2_V1_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort2_V1_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort2_V1_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort2_V2_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort2_V2_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort2_V2_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort2_V3_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort2_V3_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort2_V3_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort2_V1_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort2_V1_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort2_V1_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort2_V2_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort2_V2_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort2_V2_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort2_V3_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort2_V3_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort2_V3_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort3_C1_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort3_C1_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort3_C1_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort3_C2_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort3_C2_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort3_C2_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort3_C3_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort3_C3_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort3_C3_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort3_C1_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort3_C1_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort3_C1_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort3_C2_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort3_C2_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort3_C2_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort3_C3_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort3_C3_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort3_C3_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort3_V1_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort3_V1_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort3_V1_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort3_V2_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort3_V2_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort3_V2_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort3_V3_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort3_V3_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort3_V3_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort3_V1_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort3_V1_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort3_V1_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort3_V2_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort3_V2_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort3_V2_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort3_V3_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort3_V3_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort3_V3_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort4_C1_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort4_C1_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort4_C1_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort4_C2_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort4_C2_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort4_C2_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort4_C3_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort4_C3_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort4_C3_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort4_C1_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort4_C1_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort4_C1_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort4_C2_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort4_C2_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort4_C2_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort4_C3_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort4_C3_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort4_C3_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort4_V1_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort4_V1_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort4_V1_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort4_V2_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort4_V2_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort4_V2_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort4_V3_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort4_V3_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort4_V3_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort4_V1_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort4_V1_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort4_V1_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort4_V2_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort4_V2_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort4_V2_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort4_V3_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort4_V3_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort4_V3_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort5_C1_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort5_C1_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort5_C1_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort5_C2_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort5_C2_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort5_C2_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort5_C3_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort5_C3_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort5_C3_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort5_C1_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort5_C1_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort5_C1_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort5_C2_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort5_C2_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort5_C2_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort5_C3_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort5_C3_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort5_C3_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort5_V1_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort5_V1_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort5_V1_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort5_V2_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort5_V2_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort5_V2_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort5_V3_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort5_V3_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort5_V3_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort5_V1_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort5_V1_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort5_V1_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort5_V2_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort5_V2_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort5_V2_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort5_V3_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort5_V3_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort5_V3_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort6_C1_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort6_C1_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort6_C1_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort6_C2_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort6_C2_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort6_C2_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort6_C3_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort6_C3_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort6_C3_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort6_C1_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort6_C1_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort6_C1_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort6_C2_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort6_C2_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort6_C2_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort6_C3_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort6_C3_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort6_C3_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort6_V1_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort6_V1_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort6_V1_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort6_V2_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort6_V2_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort6_V2_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort6_V3_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort6_V3_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort6_V3_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort6_V1_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort6_V1_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort6_V1_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort6_V2_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort6_V2_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort6_V2_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort6_V3_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort6_V3_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort6_V3_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort7_C1_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort7_C1_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort7_C1_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort7_C2_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort7_C2_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort7_C2_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort7_C3_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort7_C3_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort7_C3_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort7_C1_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort7_C1_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort7_C1_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort7_C2_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort7_C2_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort7_C2_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort7_C3_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort7_C3_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort7_C3_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort7_V1_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort7_V1_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort7_V1_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort7_V2_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort7_V2_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort7_V2_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort7_V3_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort7_V3_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort7_V3_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort7_V1_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort7_V1_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort7_V1_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort7_V2_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort7_V2_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort7_V2_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort7_V3_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort7_V3_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort7_V3_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort8_C1_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort8_C1_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort8_C1_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort8_C2_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort8_C2_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort8_C2_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort8_C3_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort8_C3_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort8_C3_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort8_C1_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort8_C1_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort8_C1_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort8_C2_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort8_C2_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort8_C2_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort8_C3_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort8_C3_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort8_C3_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort8_V1_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort8_V1_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort8_V1_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort8_V2_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort8_V2_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort8_V2_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort8_V3_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort8_V3_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort8_V3_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort8_V1_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort8_V1_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort8_V1_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort8_V2_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort8_V2_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort8_V2_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort8_V3_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort8_V3_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort8_V3_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort9_C1_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort9_C1_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort9_C1_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort9_C2_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort9_C2_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort9_C2_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort9_C3_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort9_C3_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort9_C3_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort9_C1_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort9_C1_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort9_C1_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort9_C2_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort9_C2_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort9_C2_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort9_C3_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort9_C3_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort9_C3_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort9_V1_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort9_V1_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort9_V1_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort9_V2_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort9_V2_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort9_V2_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort9_V3_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort9_V3_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort9_V3_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort9_V1_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort9_V1_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort9_V1_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort9_V2_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort9_V2_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort9_V2_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort9_V3_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort9_V3_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort9_V3_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort10_C1_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort10_C1_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort10_C1_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort10_C2_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort10_C2_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort10_C2_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort10_C3_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort10_C3_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort10_C3_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort10_C1_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort10_C1_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort10_C1_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort10_C2_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort10_C2_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort10_C2_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort10_C3_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort10_C3_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort10_C3_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort10_V1_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort10_V1_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort10_V1_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort10_V2_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort10_V2_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort10_V2_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort10_V3_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort10_V3_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort10_V3_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort10_V1_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort10_V1_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort10_V1_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort10_V2_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort10_V2_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort10_V2_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort10_V3_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort10_V3_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort10_V3_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort11_C1_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort11_C1_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort11_C1_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort11_C2_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort11_C2_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort11_C2_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort11_C3_1A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort11_C3_1A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort11_C3_1A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort11_C1_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort11_C1_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort11_C1_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort11_C2_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort11_C2_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort11_C2_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort11_C3_5A_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort11_C3_5A_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort11_C3_5A_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort11_V1_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort11_V1_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort11_V1_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort11_V2_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort11_V2_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort11_V2_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort11_V3_1000V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort11_V3_1000V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort11_V3_1000V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort11_V1_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort11_V1_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort11_V1_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort11_V2_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort11_V2_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort11_V2_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
DSCPort11_V3_100V_Offset | Offsetkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort11_V3_100V_Gain | Gainkorrektur des Messkanals, see PQ16I1-1406 | float
DSCPort11_V3_100V_PhDisp | PhaseDisposition des Messkanals, see PQ16I1-1406 | float
#lastRowOfSheet

## Parameter
#Name CCU2 (Database) | Art der Aenderung | #description | unit, dataType, boundaries, default |  |  |  |  | Page on HMI ( " ." means subpage ) | Send to R5
[10 empty] | Layer: | A53_DataLayer | A53_PresentationLayer |  | A53_BusinessLayer |  |  |  | A53_middlewarelayer (name not decided yet) | R5_ConfigurationLayer | R5_BusinessLayer | R5_HW-MiddlewareLayer
modules/ value-boundaries |  |  | #unit | #datatype | #min | #max | #default |  |  | Module: | §DataBaseModule | §GridConBackendModule | §ModbusModule | §CommunicationHandlerModule | §ErrorHandlerModule | §MeasurementsA53Module | §StatemachineModule | §DSCLibA53Module | module is not planned yet | §ControlModule | §ActorModule | §MioModule | §DSCLibR5Module
#ActivePowerControl
activePowerControl_mode |  | 0 := disable 1 := Pref + P(f) 2:= Active Power Limiter | - | int | 0 | 2 | 0 |  |  |  | s |  | r | [6 empty] | r
activePowerControl_prio |  | 0 := Highest priority 3 := Lowest priority | - | int | 0 | 3 | 0 |  |  |  | s |  | r | [6 empty] | r
activePowerControl_timeConstant |  | Timeconstant Tau | s | float | 0.001f | 100.0f | 0.1f |  |  |  | s |  | r | [6 empty] | r
activePowerControl_changeRate |  | Changerate used, when setpoint has changed | p.u./s | float | 0.0f | 10.0f | 0.0f |  |  |  | s |  | r | [6 empty] | r
activePowerControl_setPoint |  | Reference value of active power control mode | p.u. | float | -1.0f | 1.0f | 0.0f |  |  |  | s |  | r | [6 empty] | r
activePowerControl_lowerVoltage |  | P(U) characteristics | p.u. | float | 0.0f | 2.0f | 1.0f |  |  |  | s |  | r | [6 empty] | r
activePowerControl_upperVoltage |  | P(U) characteristics | p.u. | float | 0.0f | 2.0f | 1.0f |  |  |  | s |  | r | [6 empty] | r
activePowerControl_lowerVoltageDroop |  | P(U) characteristics | p.u. | float | -1000.0f | 1000.0f | 0.0f |  |  |  | s |  | r | [6 empty] | r
activePowerControl_upperVoltageDroop |  | P(U) characteristics | p.u. | float | -1000.0f | 1000.0f | 0.0f |  |  |  | s |  | r | [6 empty] | r
activePowerControl_lowerVoltagePowerMax |  | P(U) characteristics | p.u. | float | -2.f | 2.0f | 0.0f |  |  |  | s |  | r | [6 empty] | r
activePowerControl_upperVoltagePowerMax |  | P(U) characteristics | p.u. | float | -2.f | 2.0f | 0.0f |  |  |  | s |  | r | [6 empty] | r
activePowerControl_lowerFrequency |  | P(F) characteristics | p.u. | float | 0.0f | 2.0f | 1.0f |  |  |  | s |  | r | [6 empty] | r
activePowerControl_upperFrequency |  | P(F) characteristics | p.u. | float | 0.0f | 2.0f | 1.0f |  |  |  | s |  | r | [6 empty] | r
activePowerControl_lowerFrequencyDroop |  | P(F) characteristics | p.u. | float | -1000.0f | 1000.0f | 0.0f |  |  |  | s |  | r | [6 empty] | r
activePowerControl_upperFrequencyDroop |  | P(F) characteristics | p.u. | float | -1000.0f | 1000.0f | 0.0f |  |  |  | s |  | r | [6 empty] | r
activePowerControl_lowerFrequencyPowerMax |  | P(F) characteristics | p.u. | float | -2.f | 2.0f | 0.0f |  |  |  | s |  | r | [6 empty] | r
activePowerControl_upperFrequencyPowerMax |  | P(F) characteristics | p.u. | float | -2.f | 2.0f | 0.0f |  |  |  | s |  | r | [6 empty] | r
activePowerControl_activePowerLimiter_limitOne |  | Powerthreshold of P-Limit-functionality | p.u. | float | -1000.0f | 1000.0f | 0.0f |  |  |  | s |  | r | [6 empty] | r
activePowerControl_activePowerLimiter_limitTwo |  | Powerthreshold of P-Limit-functionality | p.u. | float | -1000.0f | 1000.0f | 0.0f |  |  |  | s |  | r | [6 empty] | r
#ReactivePowerControl
reactivePowerControl_mode |  | 0 := disable 1 := Qref + Q(U) 2 := Power Factor Correction 3 := VDE-AR-N 4105 method a 4 := VDE-AR-N 4105 method b 5 := VDE-AR-N 4105 method c 6 := VDE-AR-N 4110 method a 7 := VDE-AR-N 4110 method b 8 := VDE-AR-N 4110 method c 9 := VDE-AR-N 4110 method d | - | int | 0 | 9 | 0 |  |  |  | s | r | r | [6 empty] | r
reactivePowerControl_prio |  | 0 := Highest priority 3 := Lowest priority | - | int | 0 | 3 | 0 |  |  |  | s | r | r | [6 empty] | r
reactivePowerControl_timeConstant |  | Timeconstant Tau | s | float | 0.001f | 100.0f | 0.1f |  |  |  | s | r | r | [6 empty] | r
reactivePowerControl_changeRate |  | Changerate used, when setpoint has changed | p.u./s | float | 0.0f | 10.0f | 0.0f |  |  |  | s | r | r | [6 empty] | r
reactivePowerControl_setPoint |  | Reference value of reactive power control mode | p.u. | float | -1.0f | 1.0f | 0.0f |  |  |  | s | r | r | [6 empty] | r
reactivePowerControl_lowerVoltage |  | Q(U) characteristics | p.u. | float | 0.0f | 2.0f | 1.0f |  |  |  | s |  | r | [6 empty] | r
reactivePowerControl_upperVoltage |  | Q(U) characteristics | p.u. | float | 0.0f | 2.0f | 1.0f |  |  |  | s |  | r | [6 empty] | r
reactivePowerControl_lowerVoltageDroop |  | Q(U) characteristics | p.u. | float | -1000.0f | 1000.0f | 0.0f |  |  |  | s |  | r | [6 empty] | r
reactivePowerControl_upperVoltageDroop |  | Q(U) characteristics | p.u. | float | -1000.0f | 1000.0f | 0.0f |  |  |  | s |  | r | [6 empty] | r
reactivePowerControl_lowerVoltagePowerMax |  | Q(U) characteristics | p.u. | float | -2.f | 2.0f | 0.0f |  |  |  | s |  | r | [6 empty] | r
reactivePowerControl_upperVoltagePowerMax |  | Q(U) characteristics | p.u. | float | -2.f | 2.0f | 0.0f |  |  |  | s |  | r | [6 empty] | r
reactivePowerControl_powerFactorCorrection_powerFactorOne |  | Limit value one for Cos(phi) control | p.u. | float | -1.0f | 1.0f | 1.0f |  |  |  | s | r | r | [6 empty] | r
reactivePowerControl_powerFactorCorrection_powerFactorTwo |  | Limit value two for Cos(phi) control | p.u. | float | -1.0f | 1.0f | 1.0f |  |  |  | s | r | r | [6 empty] | r
reactivePowerControl_powerFactorCorrection_droop |  | Parameterizable control deviation when using independent parallel control units | p.u. | float | -10.0f | 10.0f | 0.0f |  |  |  | s | [8 empty] | r
reactivePowerControl_4105_cosPhi |  | cos φ for VDE-AR-N 4105 | - | float | -1.f | 1.f | 1.f |  |  |  | s |  | r | [6 empty] | r
reactivePowerControl_4110A_U_Q0 |  | voltage at Q = 0 | p.u. | float | 0.9f | 1.1f | 1.f |  |  |  | s |  | r | [6 empty] | r
reactivePowerControl_4110A_U_max |  | max. voltage underexcided | p.u. | float | 1.f | 1.1f | 1.04f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110A_Q_max |  | max. Q underexcided | p.u. | float | 0.f | 0.33f | 0.33f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110A_U_deadband |  | voltage deadband | p.u. | float | 0.f | 0.05f | 0.f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110B_Q_EA_soll1 |  | 1. coordinate for Q | p.u. | float | -0.33f | 0.33f | 0.f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110B_Q_EA_soll2 |  | 2. coordinate for Q | p.u. | float | -0.33f | 0.33f | 0.f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110B_Q_EA_soll3 |  | 3. coordinate for Q | p.u. | float | -0.33f | 0.33f | 0.f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110B_Q_EA_soll4 |  | 4. coordinate for Q | p.u. | float | -0.33f | 0.33f | 0.f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110B_Q_EA_soll5 |  | 5. coordinate for Q | p.u. | float | -0.33f | 0.33f | 0.f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110B_Q_EA_soll6 |  | 6. coordinate for Q | p.u. | float | -0.33f | 0.33f | 0.f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110B_Q_EA_soll7 |  | 7. coordinate for Q | p.u. | float | -0.33f | 0.33f | 0.f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110B_Q_EA_soll8 |  | 8. coordinate for Q | p.u. | float | -0.33f | 0.33f | 0.f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110B_Q_EA_soll9 |  | 9. coordinate for Q | p.u. | float | -0.33f | 0.33f | 0.f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110B_Q_EA_soll10 |  | 10. coordinate for Q | p.u. | float | -0.33f | 0.33f | 0.f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110B_P_mom1 |  | 1. coordinate for P | p.u. | float | -0.1f | -1.f | -0.1f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110B_P_mom2 |  | 2. coordinate for P | p.u. | float | -0.1f | -1.f | -0.1f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110B_P_mom3 |  | 3. coordinate for P | p.u. | float | -0.1f | -1.f | -0.1f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110B_P_mom4 |  | 4. coordinate for P | p.u. | float | -0.1f | -1.f | -0.1f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110B_P_mom5 |  | 5. coordinate for P | p.u. | float | -0.1f | -1.f | -0.1f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110B_P_mom6 |  | 6. coordinate for P | p.u. | float | -0.1f | -1.f | -0.1f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110B_P_mom7 |  | 7. coordinate for P | p.u. | float | -0.1f | -1.f | -0.1f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110B_P_mom8 |  | 8. coordinate for P | p.u. | float | -0.1f | -1.f | -0.1f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110B_P_mom9 |  | 9. coordinate for P | p.u. | float | -0.1f | -1.f | -0.1f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110B_P_mom10 |  | 10. coordinate for P | p.u. | float | -0.1f | -1.f | -0.1f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110C_Qref |  | reference Q | p.u. | float | -0.33f | 0.33f | 0.f |  |  |  | s |  | r | [6 empty] | r
reactivePowerControl_4110C_Q_P1 |  | 1. point for Q | p.u. | float | -0.33f | 0.33f | -0.33f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110C_Q_P2 |  | 2. point for Q | p.u. | float | -0.33f | 0.33f | 0.f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110C_Q_P3 |  | 3. point for Q | p.u. | float | -0.33f | 0.33f | 0.f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110C_Q_P4 |  | 4. point for Q | p.u. | float | -0.33f | 0.33f | 0.33f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110C_U_P1 |  | 1. point for U | p.u. | float | 0.9f | 1.1f | 0.94f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110C_U_P2 |  | 2. point for U | p.u. | float | 0.9f | 1.1f | 0.96f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110C_U_P3 |  | 3. point for U | p.u. | float | 0.9f | 1.1f | 1.04f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110C_U_P4 |  | 4. point for U | p.u. | float | 0.9f | 1.1f | 1.06f |  |  |  | s | [8 empty] | r
reactivePowerControl_4110_cosPhi |  | cos φ for VDE-AR-N 4110 | - | float | -1.f | 1.f | 1.f |  |  |  | s |  | r | [6 empty] | r
#LoadBalancingControl
loadBalancingControl_mode |  | 0 := Phase & neutral symmetrie 1 := Symmetrie between phases 2 := Symmetrie to neutral 3 := Stern und Dreieck |  | int | 0 | 3 | 0 |  |  |  |  | r | r | [6 empty] | r
loadBalancingControl_prio |  | 0 := Highest priority 3 := Lowest priority |  | int | 0 | 3 | 0 |  |  |  |  | r | [7 empty] | r
loadBalancingControl_timeConstant |  | Zeitkonstante Tau |  | float | 0.001f | 1.0f | 0.1f |  |  |  |  | r | [7 empty] | r
loadBalancingControl_changeRate |  | Aenderungsrate bei Setpointaenderung |  | float | 0.0f | 10.0f | 0.0f |  |  |  |  | r | [7 empty] | r
loadBalancingControl_negativeSequenceControl_currentControl_level |  | Kompensationsgrad Symmetrierung im Dreieck |  | float | 0.0f | 100.0f | 100.0f |  |  |  |  | r | [7 empty] | r
loadBalancingControl_zeroSequenceControl_currentControl_level |  | Kompensationsgrad Symmetrierung im Stern |  | float | 0.0f | 100.0f | 100.0f |  |  |  |  | r | [7 empty] | r
#IslandGridControl
islandingGridControl_VqCharacteristic_setPoint |  | Sollspannung für das Inselnetz in per unit, (bezieht sich auf die Netznennspannung) | p.u. | float | 0.0f | 2.0f | 1.0f |  |  |  |  | r | r | [6 empty] | r
islandingGridControl_VqCharacteristic_changeRate |  | Spannungsänderungrate beim Anpassung des Spannungssetpoints | p.u./s | float | 0.0f | 10.0f | 1.0f |  |  |  |  | r | r | [6 empty] | r
islandingGridControl_VqCharacteristic_timeConstant |  | Zeitkonstante des Spannungsreglers | s | float | 0.001f | 1000.0f | 0.1f |  |  |  |  | r | r | [6 empty] | r
islandingGridControl_VqCharacteristic_lowerSetPoint |  | Kennlinienfunktion U(Q) | p.u. | float | 0.0f | 2.0f | 0.0f |  |  |  |  | r | r | [6 empty] | r
islandingGridControl_VqCharacteristic_upperSetPoint |  | Kennlinienfunktion U(Q) | p.u. | float | 0.0f | 2.0f | 0.0f |  |  |  |  | r | r | [6 empty] | r
islandingGridControl_VqCharacteristic_lowerDroop |  | Kennlinienfunktion U(Q) | p.u. | float | -1000.0f | 1000.0f | 0.0f |  |  |  |  | r | r | [6 empty] | r
islandingGridControl_VqCharacteristic_upperDroop |  | Kennlinienfunktion U(Q) | p.u. | float | -1000.0f | 1000.0f | 0.0f |  |  |  |  | r | r | [6 empty] | r
islandingGridControl_FpCharacteristic_setPoint |  | Sollfrequenz für das Inselnetz in per unit, (bezieht sich auf die Netznennfrequenz) | p.u. | float | 0.0f | 2.0f | 1.0f |  |  |  |  | r | r | [6 empty] | r
islandingGridControl_FpCharacteristic_changeRate |  | Frequenzsänderungrate beim Anpassung des Frequenzetpoints | p.u./s | float | 0.0f | 10.0f | 1.0f |  |  |  |  | r | r | [6 empty] | r
islandingGridControl_FpCharacteristic_timeConstant |  | Zeitkonstante des Frequenzsreglers | s | float | 0.001f | 1000.0f | 0.1f |  |  |  |  | r | r | [6 empty] | r
islandingGridControl_FpCharacteristic_lowerSetPoint |  | Kennlinienfunktion F(P) | p.u. | float | 0.0f | 2.0f | 0.0f |  |  |  |  | r | r | [6 empty] | r
islandingGridControl_FpCharacteristic_upperSetPoint |  | Kennlinienfunktion F(P) | p.u. | float | 0.0f | 2.0f | 0.0f |  |  |  |  | r | r | [6 empty] | r
islandingGridControl_FpCharacteristic_lowerDroop |  | Kennlinienfunktion F(P) | p.u. | float | -1000.0f | 1000.0f | 0.0f |  |  |  |  | r | r | [6 empty] | r
islandingGridControl_FpCharacteristic_upperDroop |  | Kennlinienfunktion F(P) | p.u. | float | -1000.0f | 1000.0f | 0.0f |  |  |  |  | r | r | [6 empty] | r
islandingGridControl_virtualImpedance_derivative |  | aktuell nicht freigegeben | - | float | 0.0f | 0.0f | 0.0f |  |  |  |  | r | r | [6 empty] | r
islandingGridControl_virtualImpedance_filterCoeff |  | aktuell nicht freigegeben | - | float | 0.0f | 0.0f | 0.0f |  |  |  |  | r | r | [6 empty] | r
#HarmonicControlGeneral
harmonicControlGeneral_mode |  | 0 := Phase & neutral symmetrie 1 := Symmetrie between phases 2 := Symmetrie to neutral 3 := Stern und Dreieck |  | int | 0 | 3 | 0 |  |  |  |  | r | r | [6 empty] | r
harmonicControlGeneral_prio |  | 0 := Highest priority 3 := Lowest priority |  | int | 0 | 3 | 0 |  |  |  |  | r | [7 empty] | r
harmonicControlGeneral_timeConstant |  | Zeitkonstante Tau |  | float | 0.001f | 1.0f | 0.1f |  |  |  |  | r | [7 empty] | r
#HarmonicStatemachine
harmonicStatemachine_maxNumberSiaTrigger |  | Maximale zulässige Anzahl von SIA Durchlaeufen innerhalb des definierten Zeitintervalls not in use |  | int | 0 | 20 | 5 |  |  |  |  | r | [7 empty] | r
harmonicStatemachine_maxNumberSiaTriggerTimeInterval |  | Zeitinervall in der die MAX_NMB_SIA_TRIGGER_I zugelassen wird not in use |  | int | 0 | 3600 | 600 |  |  |  |  | r | [7 empty] | r
harmonicStatemachine_minTimeGabForSiaTrigger |  | Mindestzeit zwischen zwei SIA-Durchlaeufen not in use |  | int | 0 | 3600 | 30 |  |  |  |  | r | [7 empty] | r
#SelectiveHarmonicControl3
selectiveHarmonicControl3_access |  | Access via HMI |  | int | 0 | 1 | 1 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl3_mode |  | 0 := DISABLE 1 := SELF COMPENSATION 2 := COMPENSATION I 3 := COMPENSATION U 4 := COMPENSATION I + Limit U 5 := COMPENSATION U + Limit U |  | int | 0 | 5 | 0 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl3_compensationLevel |  | Degree of harmonic compensation 100 % => complete harmonic compensation | % | float | 0.0f | 100.0f | 100.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl3_voltageCompensationLimit |  | Limitation of single Harmonics | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl3_voltageBlockLimit |  | Voltage distortion limit where the individual harmonic controller is blocked | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
#SelectiveHarmonicControl5
selectiveHarmonicControl5_access |  | Access via HMI |  | int | 0 | 1 | 1 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl5_mode |  | 0 := DISABLE 1 := SELF COMPENSATION 2 := COMPENSATION I 3 := COMPENSATION U 4 := COMPENSATION I + Limit U 5 := COMPENSATION U + Limit U |  | int | 0 | 5 | 1 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl5_compensationLevel |  | Degree of harmonic compensation 100 % => complete harmonic compensation | % | float | 0.0f | 100.0f | 100.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl5_voltageCompensationLimit |  | Limitation of single Harmonics | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl5_voltageBlockLimit |  | Voltage distortion limit where the individual harmonic controller is blocked | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
#SelectiveHarmonicControl7
selectiveHarmonicControl7_access |  | Access via HMI |  | int | 0 | 1 | 1 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl7_mode |  | 0 := DISABLE 1 := SELF COMPENSATION 2 := COMPENSATION I 3 := COMPENSATION U 4 := COMPENSATION I + Limit U 5 := COMPENSATION U + Limit U |  | int | 0 | 5 | 1 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl7_compensationLevel |  | Degree of harmonic compensation 100 % => complete harmonic compensation | % | float | 0.0f | 100.0f | 100.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl7_voltageCompensationLimit |  | Limitation of single Harmonics | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl7_voltageBlockLimit |  | Voltage distortion limit where the individual harmonic controller is blocked | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
#SelectiveHarmonicControl9
selectiveHarmonicControl9_access |  | Access via HMI |  | int | 0 | 1 | 1 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl9_mode |  | 0 := DISABLE 1 := SELF COMPENSATION 2 := COMPENSATION I 3 := COMPENSATION U 4 := COMPENSATION I + Limit U 5 := COMPENSATION U + Limit U |  | int | 0 | 5 | 1 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl9_compensationLevel |  | Degree of harmonic compensation 100 % => complete harmonic compensation | % | float | 0.0f | 100.0f | 100.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl9_voltageCompensationLimit |  | Limitation of single Harmonics | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl9_voltageBlockLimit |  | Voltage distortion limit where the individual harmonic controller is blocked | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
#SelectiveHarmonicControl11
selectiveHarmonicControl11_access |  | Access via HMI |  | int | 0 | 1 | 1 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl11_mode |  | 0 := DISABLE 1 := SELF COMPENSATION 2 := COMPENSATION I 3 := COMPENSATION U 4 := COMPENSATION I + Limit U 5 := COMPENSATION U + Limit U |  | int | 0 | 5 | 0 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl11_compensationLevel |  | Degree of harmonic compensation 100 % => complete harmonic compensation | % | float | 0.0f | 100.0f | 100.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl11_voltageCompensationLimit |  | Limitation of single Harmonics | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl11_voltageBlockLimit |  | Voltage distortion limit where the individual harmonic controller is blocked | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
#SelectiveHarmonicControl13
selectiveHarmonicControl13_access |  | Access via HMI |  | int | 0 | 1 | 1 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl13_mode |  | 0 := DISABLE 1 := SELF COMPENSATION 2 := COMPENSATION I 3 := COMPENSATION U 4 := COMPENSATION I + Limit U 5 := COMPENSATION U + Limit U |  | int | 0 | 5 | 0 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl13_compensationLevel |  | Degree of harmonic compensation 100 % => complete harmonic compensation | % | float | 0.0f | 100.0f | 100.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl13_voltageCompensationLimit |  | Limitation of single Harmonics | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl13_voltageBlockLimit |  | Voltage distortion limit where the individual harmonic controller is blocked | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
#SelectiveHarmonicControl15
selectiveHarmonicControl15_access |  | Access via HMI |  | int | 0 | 1 | 1 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl15_mode |  | 0 := DISABLE 1 := SELF COMPENSATION 2 := COMPENSATION I 3 := COMPENSATION U 4 := COMPENSATION I + Limit U 5 := COMPENSATION U + Limit U |  | int | 0 | 5 | 0 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl15_compensationLevel |  | Degree of harmonic compensation 100 % => complete harmonic compensation | % | float | 0.0f | 100.0f | 100.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl15_voltageCompensationLimit |  | Limitation of single Harmonics | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl15_voltageBlockLimit |  | Voltage distortion limit where the individual harmonic controller is blocked | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
#SelectiveHarmonicControl17
selectiveHarmonicControl17_access |  | Access via HMI |  | int | 0 | 1 | 1 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl17_mode |  | 0 := DISABLE 1 := SELF COMPENSATION 2 := COMPENSATION I 3 := COMPENSATION U 4 := COMPENSATION I + Limit U 5 := COMPENSATION U + Limit U |  | int | 0 | 5 | 0 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl17_compensationLevel |  | Degree of harmonic compensation 100 % => complete harmonic compensation | % | float | 0.0f | 100.0f | 100.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl17_voltageCompensationLimit |  | Limitation of single Harmonics | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl17_voltageBlockLimit |  | Voltage distortion limit where the individual harmonic controller is blocked | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
#SelectiveHarmonicControl19
selectiveHarmonicControl19_access |  | Access via HMI |  | int | 0 | 1 | 1 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl19_mode |  | 0 := DISABLE 1 := SELF COMPENSATION 2 := COMPENSATION I 3 := COMPENSATION U 4 := COMPENSATION I + Limit U 5 := COMPENSATION U + Limit U |  | int | 0 | 5 | 0 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl19_compensationLevel |  | Degree of harmonic compensation 100 % => complete harmonic compensation | % | float | 0.0f | 100.0f | 100.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl19_voltageCompensationLimit |  | Limitation of single Harmonics | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl19_voltageBlockLimit |  | Voltage distortion limit where the individual harmonic controller is blocked | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
#SelectiveHarmonicControl21
selectiveHarmonicControl21_access |  | Access via HMI |  | int | 0 | 1 | 1 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl21_mode |  | 0 := DISABLE 1 := SELF COMPENSATION 2 := COMPENSATION I 3 := COMPENSATION U 4 := COMPENSATION I + Limit U 5 := COMPENSATION U + Limit U |  | int | 0 | 5 | 0 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl21_compensationLevel |  | Degree of harmonic compensation 100 % => complete harmonic compensation | % | float | 0.0f | 100.0f | 100.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl21_voltageCompensationLimit |  | Limitation of single Harmonics | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl21_voltageBlockLimit |  | Voltage distortion limit where the individual harmonic controller is blocked | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
#SelectiveHarmonicControl23
selectiveHarmonicControl23_access |  | Access via HMI |  | int | 0 | 1 | 1 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl23_mode |  | 0 := DISABLE 1 := SELF COMPENSATION 2 := COMPENSATION I 3 := COMPENSATION U 4 := COMPENSATION I + Limit U 5 := COMPENSATION U + Limit U |  | int | 0 | 5 | 0 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl23_compensationLevel |  | Degree of harmonic compensation 100 % => complete harmonic compensation | % | float | 0.0f | 100.0f | 100.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl23_voltageCompensationLimit |  | Limitation of single Harmonics | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl23_voltageBlockLimit |  | Voltage distortion limit where the individual harmonic controller is blocked | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
#SelectiveHarmonicControl25
selectiveHarmonicControl25_access |  | Access via HMI |  | int | 0 | 1 | 1 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl25_mode |  | 0 := DISABLE 1 := SELF COMPENSATION 2 := COMPENSATION I 3 := COMPENSATION U 4 := COMPENSATION I + Limit U 5 := COMPENSATION U + Limit U |  | int | 0 | 5 | 0 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl25_compensationLevel |  | Degree of harmonic compensation 100 % => complete harmonic compensation | % | float | 0.0f | 100.0f | 100.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl25_voltageCompensationLimit |  | Limitation of single Harmonics | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl25_voltageBlockLimit |  | Voltage distortion limit where the individual harmonic controller is blocked | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
#SelectiveHarmonicControl27
selectiveHarmonicControl27_access |  | Access via HMI |  | int | 0 | 1 | 1 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl27_mode |  | 0 := DISABLE 1 := SELF COMPENSATION 2 := COMPENSATION I 3 := COMPENSATION U 4 := COMPENSATION I + Limit U 5 := COMPENSATION U + Limit U |  | int | 0 | 5 | 0 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl27_compensationLevel |  | Degree of harmonic compensation 100 % => complete harmonic compensation | % | float | 0.0f | 100.0f | 100.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl27_voltageCompensationLimit |  | Limitation of single Harmonics | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl27_voltageBlockLimit |  | Voltage distortion limit where the individual harmonic controller is blocked | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
#SelectiveHarmonicControl29
selectiveHarmonicControl29_access |  | Access via HMI |  | int | 0 | 1 | 1 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl29_mode |  | 0 := DISABLE 1 := SELF COMPENSATION 2 := COMPENSATION I 3 := COMPENSATION U 4 := COMPENSATION I + Limit U 5 := COMPENSATION U + Limit U |  | int | 0 | 5 | 0 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl29_compensationLevel |  | Degree of harmonic compensation 100 % => complete harmonic compensation | % | float | 0.0f | 100.0f | 100.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl29_voltageCompensationLimit |  | Limitation of single Harmonics | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl29_voltageBlockLimit |  | Voltage distortion limit where the individual harmonic controller is blocked | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
#SelectiveHarmonicControl31
selectiveHarmonicControl31_access |  | Access via HMI |  | int | 0 | 1 | 1 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl31_mode |  | 0 := DISABLE 1 := SELF COMPENSATION 2 := COMPENSATION I 3 := COMPENSATION U 4 := COMPENSATION I + Limit U 5 := COMPENSATION U + Limit U |  | int | 0 | 5 | 0 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl31_compensationLevel |  | Degree of harmonic compensation 100 % => complete harmonic compensation | % | float | 0.0f | 100.0f | 100.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl31_voltageCompensationLimit |  | Limitation of single Harmonics | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl31_voltageBlockLimit |  | Voltage distortion limit where the individual harmonic controller is blocked | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
#SelectiveHarmonicControl33
selectiveHarmonicControl33_access |  | Access via HMI |  | int | 0 | 1 | 1 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl33_mode |  | 0 := DISABLE 1 := SELF COMPENSATION 2 := COMPENSATION I 3 := COMPENSATION U 4 := COMPENSATION I + Limit U 5 := COMPENSATION U + Limit U |  | int | 0 | 5 | 0 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl33_compensationLevel |  | Degree of harmonic compensation 100 % => complete harmonic compensation | % | float | 0.0f | 100.0f | 100.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl33_voltageCompensationLimit |  | Limitation of single Harmonics | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl33_voltageBlockLimit |  | Voltage distortion limit where the individual harmonic controller is blocked | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
#SelectiveHarmonicControl35
selectiveHarmonicControl35_access |  | Access via HMI |  | int | 0 | 1 | 1 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl35_mode |  | 0 := DISABLE 1 := SELF COMPENSATION 2 := COMPENSATION I 3 := COMPENSATION U 4 := COMPENSATION I + Limit U 5 := COMPENSATION U + Limit U |  | int | 0 | 5 | 0 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl35_compensationLevel |  | Degree of harmonic compensation 100 % => complete harmonic compensation | % | float | 0.0f | 100.0f | 100.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl35_voltageCompensationLimit |  | Limitation of single Harmonics | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl35_voltageBlockLimit |  | Voltage distortion limit where the individual harmonic controller is blocked | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
#SelectiveHarmonicControl37
selectiveHarmonicControl37_access |  | Access via HMI |  | int | 0 | 1 | 1 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl37_mode |  | 0 := DISABLE 1 := SELF COMPENSATION 2 := COMPENSATION I 3 := COMPENSATION U 4 := COMPENSATION I + Limit U 5 := COMPENSATION U + Limit U |  | int | 0 | 5 | 0 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl37_compensationLevel |  | Degree of harmonic compensation 100 % => complete harmonic compensation | % | float | 0.0f | 100.0f | 100.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl37_voltageCompensationLimit |  | Limitation of single Harmonics | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl37_voltageBlockLimit |  | Voltage distortion limit where the individual harmonic controller is blocked | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
#SelectiveHarmonicControl39
selectiveHarmonicControl39_access |  | Access via HMI |  | int | 0 | 1 | 1 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl39_mode |  | 0 := DISABLE 1 := SELF COMPENSATION 2 := COMPENSATION I 3 := COMPENSATION U 4 := COMPENSATION I + Limit U 5 := COMPENSATION U + Limit U |  | int | 0 | 5 | 0 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl39_compensationLevel |  | Degree of harmonic compensation 100 % => complete harmonic compensation | % | float | 0.0f | 100.0f | 100.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl39_voltageCompensationLimit |  | Limitation of single Harmonics | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl39_voltageBlockLimit |  | Voltage distortion limit where the individual harmonic controller is blocked | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
#SelectiveHarmonicControl41
selectiveHarmonicControl41_access |  | Access via HMI |  | int | 0 | 1 | 1 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl41_mode |  | 0 := DISABLE 1 := SELF COMPENSATION 2 := COMPENSATION I 3 := COMPENSATION U 4 := COMPENSATION I + Limit U 5 := COMPENSATION U + Limit U |  | int | 0 | 5 | 0 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl41_compensationLevel |  | Degree of harmonic compensation 100 % => complete harmonic compensation | % | float | 0.0f | 100.0f | 100.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl41_voltageCompensationLimit |  | Limitation of single Harmonics | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl41_voltageBlockLimit |  | Voltage distortion limit where the individual harmonic controller is blocked | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
#SelectiveHarmonicControl43
selectiveHarmonicControl43_access |  | Access via HMI |  | int | 0 | 1 | 1 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl43_mode |  | 0 := DISABLE 1 := SELF COMPENSATION 2 := COMPENSATION I 3 := COMPENSATION U 4 := COMPENSATION I + Limit U 5 := COMPENSATION U + Limit U |  | int | 0 | 5 | 0 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl43_compensationLevel |  | Degree of harmonic compensation 100 % => complete harmonic compensation | % | float | 0.0f | 100.0f | 100.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl43_voltageCompensationLimit |  | Limitation of single Harmonics | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl43_voltageBlockLimit |  | Voltage distortion limit where the individual harmonic controller is blocked | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
#SelectiveHarmonicControl45
selectiveHarmonicControl45_access |  | Access via HMI |  | int | 0 | 1 | 1 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl45_mode |  | 0 := DISABLE 1 := SELF COMPENSATION 2 := COMPENSATION I 3 := COMPENSATION U 4 := COMPENSATION I + Limit U 5 := COMPENSATION U + Limit U |  | int | 0 | 5 | 0 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl45_compensationLevel |  | Degree of harmonic compensation 100 % => complete harmonic compensation | % | float | 0.0f | 100.0f | 100.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl45_voltageCompensationLimit |  | Limitation of single Harmonics | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl45_voltageBlockLimit |  | Voltage distortion limit where the individual harmonic controller is blocked | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
#SelectiveHarmonicControl47
selectiveHarmonicControl47_access |  | Access via HMI |  | int | 0 | 1 | 1 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl47_mode |  | 0 := DISABLE 1 := SELF COMPENSATION 2 := COMPENSATION I 3 := COMPENSATION U 4 := COMPENSATION I + Limit U 5 := COMPENSATION U + Limit U |  | int | 0 | 5 | 0 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl47_compensationLevel |  | Degree of harmonic compensation 100 % => complete harmonic compensation | % | float | 0.0f | 100.0f | 100.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl47_voltageCompensationLimit |  | Limitation of single Harmonics | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl47_voltageBlockLimit |  | Voltage distortion limit where the individual harmonic controller is blocked | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
#SelectiveHarmonicControl49
selectiveHarmonicControl49_access |  | Access via HMI |  | int | 0 | 1 | 1 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl49_mode |  | 0 := DISABLE 1 := SELF COMPENSATION 2 := COMPENSATION I 3 := COMPENSATION U 4 := COMPENSATION I + Limit U 5 := COMPENSATION U + Limit U |  | int | 0 | 5 | 0 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl49_compensationLevel |  | Degree of harmonic compensation 100 % => complete harmonic compensation | % | float | 0.0f | 100.0f | 100.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl49_voltageCompensationLimit |  | Limitation of single Harmonics | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl49_voltageBlockLimit |  | Voltage distortion limit where the individual harmonic controller is blocked | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
#SelectiveHarmonicControl51
selectiveHarmonicControl51_access |  | Access via HMI |  | int | 0 | 1 | 1 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl51_mode |  | 0 := DISABLE 1 := SELF COMPENSATION 2 := COMPENSATION I 3 := COMPENSATION U 4 := COMPENSATION I + Limit U 5 := COMPENSATION U + Limit U |  | int | 0 | 5 | 0 |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl51_compensationLevel |  | Degree of harmonic compensation 100 % => complete harmonic compensation | % | float | 0.0f | 100.0f | 100.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl51_voltageCompensationLimit |  | Limitation of single Harmonics | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
selectiveHarmonicControl51_voltageBlockLimit |  | Voltage distortion limit where the individual harmonic controller is blocked | % | float | 0.0f | 100.0f | 0.0f |  |  |  |  | r | [7 empty] | r
#ACDCConverterControl
acdcConverterControl_dcVoltageLevelControlMode |  | 0 := DISABLE1 1 := CONSTANT: Setpoint is calculated using nominal voltage 2 := VARIABLE 3 := MANUEL |  | int | 0 | 3 | 1 | [5 empty] | r | [6 empty] | r
acdcConverterControl_dcVoltageSetPoint |  | DC Setpoint der Gruppe 1 | V | float | 0.0f | 1500.0f | 800.0f | [5 empty] | r | [6 empty] | r
acdcConverterControl_upperActivePowerLimit |  | Power Limiter upper Limit | W | float | 0.0f | 1.0f | 1.0f | [5 empty] | r | [6 empty] | r
acdcConverterControl_lowerActivePowerLimit |  | Power Limiter upper Limit | W | float | -1.0f | 0.0f | -1.0f | [5 empty] | r | [6 empty] | r
acdcConverterControl_fanSpeed |  | FanSpeed for IPU Fans. Hint: FanControl of IPU is not overwritten with this user setpoint. The user setpoint is only applied, if fan control of ipu calculates a lower fan speed than user fan speed. | % | float | 0.0f | 1.0f | 0.0f | [5 empty] | r | [6 empty] | r
#Statemachine
paramHarmonicStatemachineMaxNumberSiaTrigger |  | not in use |  | int | 0 | 20 | 5 | [5 empty] | r |  |  |  | r
paramHarmonicStatemachineMaxNumberSiaTriggerTimeIntervall |  | not in use |  | int | 0 | 3600 | 600 | [5 empty] | r |  |  |  | r
paramHarmonicStatemachineMinTimeGabForSiaTrigger |  | not in use |  | int | 0 | 3600 | 30 | [5 empty] | r |  |  |  | r
gridControlMode |  | 0 = GRID_FOLLOWING_MODE 1 = GRID_FORMING_MODE , not in use |  | int | 0 | 1 | 0 | [5 empty] | r |  |  |  | r
blackstartApproval |  | 0 = BLACKSTART_DISABLED 1 = BLACKSTART_ENABLED , not in use |  | int | 0 | 1 | 0 | [5 empty] | r |  |  |  | r
paramActor0Enable |  | not in use |  | int | 0 | 1 | 0 | [5 empty] | r |  |  |  | r
paramActor1Enable |  | not in use |  | int | 0 | 1 | 0 | [5 empty] | r |  |  |  | r
paramActor2Enable |  | not in use |  | int | 0 | 1 | 0 | [5 empty] | r |  |  |  | r
paramActor3Enable |  | not in use |  | int | 0 | 1 | 0 | [5 empty] | r |  |  |  | r
paramActor4Enable |  | not in use |  | int | 0 | 1 | 0 | [5 empty] | r |  |  |  | r
paramActor5Enable |  | not in use |  | int | 0 | 1 | 0 | [5 empty] | r |  |  |  | r
#ParamGridConBackend
operatorMode |  | 0 = Only Remote 1 = Only Local |  | int | 0 | 1 | 0 | [5 empty] | r
#lastRowOfSheet
version-history: